## Cover
57 Rathbeale Road
CRC Omni Unit 48A — Master Findings Register v0.3
Sprint Day 1 (Wed 27-May-2026) — v0.1 baseline + Round 1 (5 subagents) + Round 2 (5 subagents, drawings + healthcare)
Severity rollup (v0.3) |  |  | By Discipline (Total · CRITICAL · HIGH)
CRITICAL | 28 |  | ARCHITECTURAL | 64 | 8 | 24
HIGH | 94 |  | ARCHITECTURAL/COORDINATION | 3 | 0 | 1
MEDIUM | 92 |  | C&S | 53 | 3 | 11
LOW | 22 |  | CONTRACT/PACK | 3 | 3 | 0
TOTAL | 268 |  | CROSS-DISCIPLINE | 5 | 0 | 1
|  |  | ELECTRICAL | 47 | 5 | 20
|  |  | FIRE | 8 | 0 | 4
|  |  | FIRE/COORDINATION | 12 | 3 | 6
|  |  | HEALTHCARE | 23 | 3 | 7
Sprint progress vs project-brief working targets |  |  | M&E | 4 | 0 | 1
|  |  | MECHANICAL | 46 | 3 | 19
Severity | Project brief target | v0.3 actual (Day 1) | Variance
CRITICAL | 3 | 28 | +25 (9.3× target)
HIGH | 18 | 94 | +76 (5.2× target)
MEDIUM | 24 | 92 | +68 (3.8× target)
LOW | 15 | 22 | +7 (1.5× target)
Headline
The Day-1 full review exceeds the project-brief CRITICAL target by 9.3× and the HIGH target by 6.2×. The pack is not in pre-issue cleanup territory — it is in fundamental remediation territory. H-001 alone (every drawing title block reads 'Adults with Disabilities' against a CRC Children's Disability Network Team brief) questions whether the design is for the right user group. Variation exposure quantification (Day 6) will substantially exceed the original €270k upper bound. Issuing on 10-Jun-2026 with this pack would expose the Employer to multi-line PW-CF5 Clause 9 / Clause 10 claims.

## All Findings
Finding ID | Severity | Discipline | Category | Document | Section / Location | Regulatory basis | Operational risk | Recommended action | Evidence quote | Source | Owner | Status
A-009 | CRITICAL | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section K10 clauses 115A/115B/115C/115D (and K10/145 wall lining) | TGD-B Vol.2 (2024) Table B4 & §3.5.5/§3.5.7 (compartment walls in non-residential institutional/assembly buildings require min. 60 min fire resistance); FSC Condition 3 (granted 19/08/2025) which expressly requires compartment walls to TGD-B 2024 §3.5.5, 3.5.7, 3.5.9-3.5.14 and Appendix A. | Spec defines every dry-lining partition (Wall Types 1-4) as 'REI 30 or better' only, with no 60-minute compartment wall type. Contractor will tender on REI 30, leaving the compartment walls required by the FSC un-priced; on site this becomes a Compensation Event under PW-CF5 Clause 10.6 and exposes the project to a non-compliant FSC implementation and BCAR Ancillary Certificate refusal. | Insert a new clause K10/115F 'Compartment Wall Partition - REI 60' (single or twin row studs to suit, 2 x 15mm Type F plasterboard each side, mineral wool 50mm, full Appendix A detail set including head, base, abutment and service-penetration treatment per TGD-B 2024 §3.5.7). Annotate each partition type on a Wall Types plan against fire-cert designation. Issue as Tender Addendum. | Fire resistance of complete partition assembly: To BS EN 13501-2. REI 30 or better ... Other requirements: Fire-stopping around services as section P12 if it is a designated fire wall. Refer to Fire Cert drawings | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.58-62 (Section K10 cl. 115A-115E) | ARCH_DESIGNER | OPEN
A-010 | CRITICAL | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification (and Sanitary Schedule 40006) | N13 Sanitary appliances; N25 Permanent access and safety equipment; Sanitary Schedule 40006 (Item HOI001) | Changing Places Consortium Technical Specification (UK/IRE 2022): ceiling-mounted XY-track hoist required, SWL not less than 200 kg, with structural support designed for 2.5 x SWL; HIQA National Standards for Residential Services for Adults with Disabilities Theme 5; Safety, Health and Welfare at Work (General Application) Regs 2007 Part 4; PUWER 2008. | Sanitary Schedule 40006 (room 0.06 C/P WC) lists 'HOI001 - TRACK HOIST - ceiling mounted H style full coverage of space'. Architectural Spec (N13 and N25) is silent on manufacturer, SWL, voltage, charging point, track configuration, structural pad-stones/back-plates, and commissioning standard. Project brief flags an unresolved CARBITAN vs ARJO vs SEA conflict from earlier issues — none of the three is in the current Arch Spec. Contractor will price the cheapest generic hoist, the Structural design will not have a co-ordinated bearing pad, and HIQA registration will be refused on opening. | Add new clause N25/220 'Ceiling-mounted Patient Hoist System' naming the approved manufacturer (HSE Estates currently approves ARJO Maxi Sky 2 or equivalent), SWL 200kg minimum, full ceiling-track coverage of room 0.06 plus traverse to adjacent shower, with structural reaction loads (typically 2.5 kN point load each track support) to be co-ordinated with Structural Engineer prior to slab/ceiling pour. Reference HBN 00-02 and HSE Estates Buildings Technical Note BTN-04 (Hoists). Confirm in writing with Employer which of CARBITAN / ARJO / SEA is the governing brand and freeze in Tender Addendum. | HOI001 TRACK HOIST - ceiling mounted H style full coverage of space | 11606-XX-ZZZ-SH-RHA-AR-40006- Sanitary Schedules.pdf (room 0.06 C/P WC); 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.143-145 (N25) - no hoist clause | EMPLOYER | OPEN
A-011 | CRITICAL | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section N15 'Internal fire and safety signage systems', clause 270 'Fire performance' | TGD-B Vol.2 (2024) §3.5 Table 3.6 (linings in protected escape routes require Class B-s3,d2 to BS EN 13501-1 minimum). BS 5499-4:2013 §4.3. | Specifying Class C for escape signage substrate is sub-compliant with TGD-B 2024 for materials lining protected escape routes. Refusal of BCAR Certificate of Compliance on Completion or FSC enforcement action would follow. | Amend N15/270 to: 'Reaction to fire: Standard: To BS EN 13501-1; Class B-s1,d0 to all escape signage substrates and any photoluminescent backing.' Cross-reference with Fire Strategy Report Cond. 3. | 270 Fire performance 1. Description: OF FIRE ESCAPE SIGNAGE SYSTEM 2. Reaction to fire 2.1. Standard: To BS EN 13501-1 2.2. Class: C | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.141 (N15/270) | ARCH_DESIGNER | OPEN
A-100 | CRITICAL | ARCHITECTURAL | DOCUMENT_HYGIENE | Windows & External Doors Type Elevations & Schedules | Drawing 11606-XX-XXX-SH-RHA-AR-40002 | PW-CF5 ED tender completeness; CWMF doc-hygiene; TGD L 2022 (window/door U-values must be tenderable); TGD M 2022 (external door clear widths/glazing manifestation) | PDF file at 40002 contains stair-section content only — no window types, no external door schedule, no glazing spec, no U-values. Tenderers cannot price windows, ext doors, glass, ironmongery to ext doors, or trickle vents. Issuing pack at tender is non-compliant and will trigger a tender-stage RFI on the highest-cost facade element. | Re-issue 40002 with the correct content: Window Types W0.001–W0.0xx (frame system, glazing make-up, U-value W/m²K, g-value, opening lights, restrictor, manifestation, trickle vent area), External Door Types XD0.0xx (leaf, glazing, threshold, ironmongery set ref, security rating, U-value), Window Boards, integrated blind cassettes, and full coordinated Schedule. Confirm before 10-Jun tender issue. | PDF 40002 page 1 and page 2 both render the stair layout (24 risers, Roof Landing, Precast Concrete Stair 3465mm rise) identical to 25001. No window/CW/ext-door content present. | 11606-XX-XXX-SH-RHA-AR-40002- Windows & External Doors Type Elevations & Schedules.pdf | ARCH_DESIGNER | OPEN
A-101 | CRITICAL | ARCHITECTURAL | DOCUMENT_HYGIENE | Curtain Walls Type Elevations & Schedule | Drawing 11606-XX-XXX-SH-RHA-AR-40003 | PW-CF5 ED tender completeness; TGD B Vol 2 (CW fire-stopping at slab edge); TGD L 2022 (CW U-value, g-value); TGD K (glazing impact safety) | PDF 40003 also contains only stair content — no CW-01, CW-09 (referenced on Elevations 20001) elevations, no schedule, no spider/transom/mullion details, no spandrel make-up. Highest visual-quality facade element is unpriceable. Will create variation exposure post-award. | Issue corrected 40003 with: CW-01…CW-NN bay elevations at 1:25, glazing make-up table (U-value, g-value, acoustic Rw), aluminium colour ref, structural sealant/cap details, slab-edge fire-stopping (TGD B Vol 2 ref), interface to brick reveal, integrated blinds (if any). Cross-reference all CW marks on Elevations sheet 20001. | PDF 40003 pages 1–2 both render stair layout content (Stair 24 risers 9.85 m²) identical to 25001. CW-01, CW-09 referenced on 20001 but no CW elevation/schedule found anywhere in the issued pack. | 11606-XX-XXX-SH-RHA-AR-40003- Curtain Walls Type Elevations & Schedule.pdf | ARCH_DESIGNER | OPEN
A-102 | CRITICAL | ARCHITECTURAL | COMPLIANCE | C/P WC Room Layout & Sanitary Schedule | Room 0.06, Drawings 60006 + 40006 | Changing Places Consortium 2019 (Ireland) §4.2 – mandatory peninsular WC pan with min 1000mm transfer space each side; HIQA Standard 1.6 (dignity & privacy) | Sanitary schedule for Room 0.06 lists WCH005 'CANTILEVER, hospital pattern' (wall-hung corner WC) — NOT a peninsular WC. Changing Places certification requires a peninsular pan accessible from both sides for hoist transfer. As specified, the C/P WC fails Changing Places certification and HIQA registration of the unit will be at risk. | Replace WCH005 in Room 0.06 with peninsular WC (e.g. AKW Livenza-P or equivalent) projecting 800mm from rear wall with 1000mm clear each side; reissue 60006 plan and sanitary schedule 40006. Confirm with HSE Estates that CR2C unit must be 'Registered Changing Places' (not just enhanced accessible WC). | 40006 Room 0.06: 'WCH005 WC/toilet pan with seat & cover, 750 mm projection CANTILEVER, hospital pattern, rimless pan, vitreous china 1'. Plan 60006 elevations show pan against wall, not peninsular. | 11606-XX-ZZZ-SH-RHA-AR-40006 + 11606-XX-L00-DR-RHA-AR-60006 | ARCH_DESIGNER | OPEN
A-103 | CRITICAL | ARCHITECTURAL | COMPLIANCE | C/P WC Room Layout & Sanitary Schedule | Room 0.06, Drawings 60006 + 40006 | Changing Places Consortium 2019 §4.3 – height-adjustable adult-sized changing bench (min 1800×800mm, electrically height-adjustable 300–1000mm, SWL ≥200kg); HIQA Standard 5 | Sanitary schedule 40006 for Room 0.06 omits BNH900 (changing bench) from the list — only shown as a 2D symbol on elevations of 60006. As tendered, no specification, no SWL, no actuator, no fixings; bench cannot be priced or installed correctly. C/P WC will not be commissionable. | Add adult-sized height-adjustable changing bench to sanitary schedule 40006 Room 0.06: e.g. Pressalit R8581 or equivalent, 1800×800mm, electric, SWL 200kg, with control pendant, including fixing to engineered backing plate (cross-ref ARCH details for structural pull-out). Confirm electrical supply, IP rating, and BS EN 60601 compliance. | 40006 Room 0.06 sanitary list: BAS110, BRA021, CIS005, HOI001, SHO018, SHO020, TAP289, WAS107, WCH005 — no BNH900 line item, no SWL, no make/model. BNH900 appears only as ADB symbol on 60006 elevation A. | 11606-XX-ZZZ-SH-RHA-AR-40006 + 11606-XX-L00-DR-RHA-AR-60006 | ARCH_DESIGNER | OPEN
A-107 | CRITICAL | ARCHITECTURAL | COMPLIANCE | Internal Finishes Schedule — Kitchen 0.17 | Drawing 40009 row 0.17 | IS EN 16282-7:2017 commercial kitchen ventilation/finishes; HSE Food Safety Authority Ireland (Reg EC 852/2004) – walls, ceilings and overhead fixtures must be of smooth, impervious, non-absorbent, washable, non-toxic material; FSC Condition 5 (kitchen as place of special fire risk) | Kitchen 0.17 walls specified as 'Washable matt emulsion paint, enhanced durability, Colour - White'. Paint is absorbent, not impervious, fails Reg 852/2004 Annex II Ch I. EHO will not pass kitchen at HIQA registration. Re-clad cost in occupation phase. | Change Kitchen 0.17 wall finish to PVC hygienic wall lining (Altro Whiterock Satins or equiv) full height to ceiling, welded seams, coved to floor and ceiling, behind appliances and at splashback. Update 40009 row 0.17. Match approach already used in WC/Shower/Cleaners Store rows. | 40009 row 0.17 KITCHEN Wall Finish: 'Washable matt emulsion paint, enhanced durability, Colour - White'. | 11606-XX-ZZZ-SH-RHA-AR-40009 | ARCH_DESIGNER | OPEN
C-001 | CRITICAL | CONTRACT/PACK | DOCUMENT_HYGIENE | Multiple — Arch register, M&E issue sheet, Fire Stage 2C report | Project title block / header across all 3 packs | PW-CF5 Conditions of Contract Clause 1.1 (definitions); SI 9/2014 Reg 5 (consistency of design info); CWMF ARM4 §A1.2 (single project identity) | Three different project descriptors create ambiguity over what is being tendered. At award, the executed contract may reference a description that does not match drawings or specifications, creating dispute potential and challenging BCAR compliance. | Issue a single project descriptor instruction: '57 Rathbeale Road CRC Children's Disability Network Team — Day Care Centre, Swords, Co. Dublin K67 EP62'. Update all discipline pack title blocks to this exact descriptor before tender issue. Confirm legal Employer entity (HSE per M&E sheet vs. CRC per project brief vs. Building Owner) on FOT Schedule Part 1. | M&E Drawing Issue Sheet: 'HSE HEALTH CARE CENTRE / RATHBEALE ROAD'; Arch Drawing Register: 'Project Title: Rathbeale Rd Day Care / Client: HSE'; Fire Report: '57 Rathbeale Road, Swords, Co. Dublin, K67 EP62'. | 11606-RG-RHA-AR-0001 Drawing Register p.1 / 1743_Drgissue 2C Sheet 1 / 22481-Stage 2C Report p.1 | EMPLOYER | OPEN
C-002 | CRITICAL | CONTRACT/PACK | DOCUMENT_HYGIENE | All discipline registers | Issue dates across discipline packs | CWMF ARM4 §A2 (coherent tender pack issue); SI 9/2014 Reg 9 (designer responsibility for issued info) | Tender pack is not a single coherent issue. Tenderers cannot rely on a single 'issue date' as the price-baseline. Variations may be claimed against information issued at different times. | Reissue all discipline packs to a single coordinated tender issue date with consistent revision codes. State 'Issued for Tender — DD-MMM-2026' on every title block. Lock CDE issue date. | Arch: P08-S (no explicit date on register); C&S: 08/05/26; M&E: 13-MAY-26; Fire: 31/03/2026. | All 4 register PDFs | ER | OPEN
C-003 | CRITICAL | CONTRACT/PACK | COMPLIANCE | Fire Part B Compliance Report (22481-Stage 2C Report) | Notes 12-15 (p.5) | SI 496/2009 Building Control Regulations §11; SI 9/2014 (BCAR); TGD-B 2024 | Existing granted FSC dated 19/08/2025 with 7 conditions. Design changes 31/03/2026 (external store under stairs, bin→bike store, Activity Room 13 reconfig) formally determined by SFPO Keith Boland 08/04/2026 to require REVISED FSC and DAC. Tenderer must price for revised FSC submission process AND for compliance with both the original 7 conditions and any conditions on the revised grant. Commencement may issue on existing FSC, but occupation is blocked until revised FSC and DAC are granted. | (1) Add explicit clause in Preliminaries: 'Contractor shall allow for compliance with the granted FSC and its 7 conditions, and shall allow for cooperation with Design Team submission of revised FSC and DAC during construction. Occupation is contingent on grant of revised FSC and DAC.' (2) Issue all 7 FSC conditions as a tenderer-facing schedule. (3) Confirm position on Activity Room 13 / bike store / external store scope freeze before tender issue. | Fire Report Note 14: 'It was determined on 08/04/2026 following a formal response from SFPO Keith Boland that the works were not considered minor enough such that under Section 11 of SI 496 of the Building Control Regulations a revised FSC and DAC would be required.' Note 15: 'commencement can still be issued on the basis of the existing granted FSC. However, the Revised FSC and DAC must be submitted an granted during the construction phase before the building is occupied.' | 22481-Stage 2C Report-Part B Compliance.pdf p.5 | ER | OPEN
E-100 | CRITICAL | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Electrical Specification | §2.05 Standards, Rules and Regulations / §4.02 / §4.04 | I.S. 10101:2020+A1:2024 (National Rules for Electrical Installations) per FSC Cond 6; SI 423 of 2020; ETCI superseded by NSAI National Rules | Spec lists BS 7671:2018 (UK standard), ETCI Rules, IEE Wiring Regulations 16th Edition, BS 5486, IEC 144, BS 5420, BS 6346:1989, BS 8724:1990, BS 4568-1970 etc as primary references. Contractor is contractually obliged to comply with these obsolete/non-Irish standards. Risk of installation being non-compliant with FSC Cond 6, RECI/SafeElectric refusal to certify, and HSE refusal to accept handover. Cost & programme impact during construction once non-conformance is discovered. | Re-issue Sections 2.05, 4.02, 4.04, 4.05, 4.06, 4.09, 4.17, 5.01, 5.02, 5.03, 5.04, 5.06, 5.07, 6.01, 7.01, 7.03, 8.02, 10.01, 12.00 with all references aligned to I.S. 10101:2020+A1:2024. Delete BS 7671:2018, ETCI, IEE 16th Ed references. Replace BS 5486 with I.S. EN 61439 series. Replace BS 6346/BS 8724 with current IEC/EN cable standards. | BS 7671:2018, Requirements for Electrical Installations, including amendments... National rules for Electrical Installations as issued by the Electro Technical Council of Ireland... IS 10101 Wiring Rules by NSAI [listed last]; §4.02 'Regulations for Electrical Installations as published by the I.E.E. (Latest edition); BS 5486 Part I - Form 3; IEC 439'; §7.01 'effectively earth the whole of the electrical installation in accordance with the 16th Edition of the IEE wiring regulations' | Electrical Specification .pdf | EE_DESIGNER | OPEN
E-101 | CRITICAL | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Electrical Specification | §4.04 Rating and service conditions | I.S. 10101:2020+A1:2024 §312.2 Earthing Arrangements; ESB Networks Code; domestic/healthcare LV connections in Ireland are typically TN-C-S (PME) at the cut-out, not TN-S | Spec states 'a 415 volt, 50 Hz, 3 phase, 4 wire, solidly earthed (TN-S) system, with a maximum fault level of 50 KA'. ESB Networks in Ireland generally provide TN-C-S supply. TN-S is rare and would require dedicated cable from substation. Earthing design (sizes of CPC, supplementary bonding, RCD strategy) is fundamentally different between TN-S and TN-C-S. Also 50 kA fault level is unverified for a small day-care centre — typical ESB cut-out fault current at LV is 16–25 kA. Over-specifying switchgear adds cost; mis-specifying earthing system creates safety risk. | Obtain ESB Networks Quote/Connection Offer confirming (a) earthing system (TN-C-S expected), (b) prospective fault current at the cut-out (PSCC) and (c) external earth fault loop impedance Ze. Re-issue §4.04, §7.0 Earthing with verified ESB data. Confirm switchgear icw rating matches actual PSCC + safety factor. | §4.04 'The switchgear shall be designed for continuous operation on a 415 volt, 50 Hz, 3 phase, 4 wire, solidly earthed (TN-S) system, with a maximum fault level of 50 KA' | Electrical Specification .pdf | EE_DESIGNER | OPEN
E-102 | CRITICAL | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Drawing 1743_69(01) — SDB Schematic | SDB 01 & SDB 02 distribution | I.S. 10101:2020+A1:2024 §531.3.3 — Type A RCDs minimum for general use; Type B mandatory where DC fault currents possible (PV, EV chargers, VSDs, heat-pump inverters) | SDB schematics show generic 30mA RCDs/RCBOs feeding circuits that include EV car charger, PV inverter, heat-pump compressors and VSD-driven MVHR fans. PV inverter and EV charger inject DC residual currents that 'blind' Type AC and Type A RCDs, defeating earth-fault protection — established cause of electrocution. RCBO type (AC / A / F / B) is not stated on any schematic or schedule. Risk: latent loss of earth-fault protection on critical circuits at a healthcare day-care for vulnerable users. | Mark every RCD/RCBO on 1743_69(00), (01) and (02) with mandatory type: Type B at PV AC isolator, EV charger, heat-pump compressor, MVHR VSDs and lift (if any); Type A elsewhere. Add note to spec §4.09 making Type B mandatory for these circuits and prohibiting downstream Type AC. | §4.09 'Final circuit distribution MCB's and combined RCD/MCB's shall be rated as shown on the drawings... RCB/MCB's shall have a rated earth leakage trip sensitivity of 30mA and shall be capable of responding a DC component in the earth leakage current.' [Vague — does not specify Type A vs Type B; drawings 69(00)/(01) do not call out RCD type] | 1743_69_00.pdf; 1743_69_01.pdf; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-103 | CRITICAL | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Electrical Specification | §12.20 Lightning Protection System | I.S. EN 62305-2 — Risk Assessment; Project Quality Control; CDM equivalent (SHWWAW Construction Regs) | Specification §12.20 describes the project as 'School Type Building located at Convent Hill, Ballina, Co. Mayo. New Build Concrete and Steel Structure over 2 levels. Ground / 1st + Roof Over. Highest Point of Building above Ground Level _ 11.0 m'. This is verbatim text from a different project. The actual building is a SINGLE-STOREY day-care centre at 57 Rathbeale Road, Swords. Contractor would price lightning protection on wrong building geometry, wrong height, wrong occupancy (Class 'School' vs 'Healthcare day-care'). Direct contradicts FSC Cond 6 evidencing risk assessment for actual structure. This same cut-paste error was flagged in Round 1 and persists. | REJECT spec §12.20 in current form. Re-write specifically for 57 Rathbeale Road CRC Omni Unit: single-storey day-care, ground floor only (no first floor), state actual building height (parapet level), state actual roof area & geometry, state Loss L1 (loss of human life) due to vulnerable healthcare day-users. Provide IS EN 62305-2 risk assessment as appendix to spec. Confirm Down-conductors hidden in wall make-up (currently stated) is consistent with actual single-storey structure. | §12.20 'School Type Building located at Convent Hill, Ballina, Co. Mayo. New Build Concrete and Steel Structure over 2 levels. Ground / 1st + Roof Over. Highest Point of Building above Ground Level _ 11.0 m - Street Level to Highest Roof Point - It is Noted that the Roof Structure is of a Steel Construction.' | Electrical Specification .pdf | EE_DESIGNER | OPEN
E-104 | CRITICAL | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Electrical Specification | §10.17 School Lighting Notes (Primary & Secondary) / §12.16 Wiring for External Vehicle and Pedestrian Gates | Project Description (HSE Day-care, no school) / FIDIC-equivalent PW-CF5 §2.0 Description of Works | Spec §10.17 contains an entire section titled 'School Lighting Notes (Primary & Secondary)' with school-specific clauses: 'no longer a requirement to have manual switching on the row of light fittings nearest the teaching wall', 'two way switching of the classroom lights in the vicinity of the teachers desk', 'In 16 classroom schools and over', 'Principal/Caretaker', etc. §12.16 references 'external gates' likely from another commercial project. Spec also references BoQ items '62-14 classroom trunking system' and induction loops in 'classrooms and GP Hall'. None of this applies to a 12-room day-care centre. Contractor will price phantom scope and dispute later as variation; risk to tender comparability and price certainty. | Delete §10.17 entirely. Strip every reference to 'school', 'classroom', 'Principal', 'GP Hall', 'teaching wall' from spec body and BoQ summary. Re-issue §10.x lighting controls with day-care-specific requirements: tunable white in sensory rooms (DT 0.012), absence detection in therapy rooms, manual-off in administrative areas, daylight harvesting at perimeter zones, CIBSE LG7 §5 lux levels. | §10.17 'School Lighting Notes (Primary & Secondary): All lighting installations operating in conjunction with automatic dimming to Off lighting controls and absence detection must have manual On/Off/dimming switching arrangements via push type retractable light switches... There is no longer a requirement to have manual switching on the row of light fittings nearest the teaching wall... In 16 classroom schools and over...' | Electrical Specification .pdf | EE_DESIGNER | OPEN
H-001 | CRITICAL | HEALTHCARE | BRIEF_OPERATIONAL_MISMATCH | 11606-XX-L00-DR-RHA-AR-11001 GA Plan Ground Floor (and ALL drawing title-blocks across the pack) | Title-block / Project description | HSE Capital Works Management Framework Stage 2C — the Schedule of Accommodation must match the operational brief. HIQA National Standards differ materially between adult disability services and Children's Disability Network Team (CDNT) services (paediatric safeguarding, age-appropriate sanitaryware, observation, parent areas). | Every drawing in the Stage 2C pack is titled 'Construction of Day Centre for Adults with Disabilities at Rathbeale Road, Swords, Co. Dublin'. The Employer brief (and this review) treat the building as a CRC Children's Disability Network Team day-care centre. The two operational models drive fundamentally different room sizing, sanitaryware, safeguarding, signage and parent/family-zone requirements. If the design has been developed against an 'adults' brief and is now to be operated as a paediatric CDNT, the entire room data sheet basis is wrong — paediatric WCs, basins, vision panels, child window restrictors, parent waiting and changing facilities are all absent. Risk of total brief rework post-tender or, worse, an unsuitable facility delivered to HIQA on day one. | RFI to Employer (HSE Dublin North East) — formally confirm operational user: (a) Adult Disability Day Centre, OR (b) CRC Children's Disability Network Team. Until clarified, all paediatric-specific findings below remain OPEN against ARCH_DESIGNER. If (b) is correct, the entire FF&E and sanitary schedule requires re-issue with paediatric variants and a paediatric/parent-zone gap analysis must precede tender issue on 10-Jun-2026. | PROJECT: Construction of Day Centre for Adults with Disabilities at Rathbeale Road, Swords, Co. Dublin (drawing title-block, every architectural sheet, P08-S, 08/05/2026) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\11000_GA Plans\11606-XX-L00-DR-RHA-AR-11001- GA Plan - Ground Floor.pdf | EMPLOYER | OPEN
H-002 | CRITICAL | HEALTHCARE | CHANGING_PLACES_NON_COMPLIANCE | 11606-XX-L00-DR-RHA-AR-53001 C/P WC Laid to Falls + 11606-XX-ZZZ-SH-RHA-AR-40008 FF&E Totals | Room 0.06 C/P WC — 14.24 m² | Changing Places Consortium Specification (2019) + BS 8300-2:2018 §18.6: minimum 12 m² with minimum internal dimensions 4000 mm × 3000 mm; height-adjustable adult changing bench (electric, 1800×800 minimum, 300–1000 mm travel); ceiling-track hoist covering bench AND WC AND shower; peninsular WC with 1000 mm transfer space EACH side; full-length privacy screen; shower facility with central drainage gully. NDA Building for Everyone Vol 5 §5.4. | Drawing 53001 shows internal clear dimensions 3356 mm (W) × 4324 mm (D) — width is 644 mm SHORT of the 4000 mm required by Consortium spec. The FF&E schedule (AR-40008) lists ONLY a single ceiling H-track (HOI001), a single privacy screen (SCR960), and grab rails — no height-adjustable changing bench (CAB033 absent), no shower head, no shower valve and no central floor gully are scheduled in this room. The plan shows only WC, basin and a hoist track; the bench is implied by dashed lines but no equipment is specified. As designed the room WILL FAIL Changing Places registration with the Consortium and HIQA accessibility audit; CRC parents will be unable to safely change a teenage or adult-sized service user. | ARCH_DESIGNER to (a) reconfigure room to achieve 4000×3000 mm clear internal — extend wall onto Corridor 02 by ~700 mm or re-allocate ACC WC 0.05 footprint; (b) add electric height-adjustable adult changing bench to FF&E (Pressalit Select R8581 or equal-approved); (c) add overhead shower with central floor gully (drainage already shown laid-to-falls); (d) confirm hoist track covers bench + WC + shower zones (cross-ref with S — ceiling structural loading per BS EN 10535); (e) add Consortium registration intent to specification. | 0.06 C/P WC 14.24 m²; clear 3356 × 4324 mm shown on AR-53001. FF&E AR-40008: SCR960 PRIVACY SCREEN ×1, HOI001 TRACK HOIST H-style ×1, BAS110 Changing Places Toilet Sink ×1 — no CAB033 changing bench, no shower valve in this room. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\50000_Details\11606-XX-L00-DR-RHA-AR-53001- Changing Room - Laid to Falls.pdf | ARCH_DESIGNER | OPEN
H-003 | CRITICAL | HEALTHCARE | PAEDIATRIC_SANITARYWARE_MISSING | 11606-XX-ZZZ-SH-RHA-AR-40006 Sanitary Schedule | All Accessible WCs (0.05, 0.09, 0.11, 0.22, 0.29, 0.30) + Cleaners 0.03 + Group Therapy 0.08 + Activity 0.15/0.20 + Dining 0.16 | HBN 00-10 Welfare Facilities §3.4 (children's facilities); BS 8300-2 Table 8 (paediatric pan heights 305 mm at age 5, 380 mm at age 11); HSE Estates technical guide for paediatric facilities; HIQA National Standards for Residential Services for Children with Disabilities (privacy/dignity requires age-appropriate fittings). | Sanitary Schedule AR-40006 specifies WCH005 'cantilever 750 mm projection, hospital pattern' (adult pan height ~450 mm) in EVERY accessible WC, and BAS105 (adult small wash basin) throughout. CRC CDNTs serve children aged 0–18 with wide developmental range. There are NO paediatric pans, NO low-level (380–510 mm) child WCs, NO paediatric basins at 600 mm rim height in any room. Children will need to be lifted onto adult pans — fall risk, manual-handling injury risk to staff, dignity breach. HIQA inspectors will cite this on first visit. | Pending H-001 clarification: if CDNT brief confirmed, ARCH_DESIGNER to add minimum one paediatric WC + paediatric basin in each of the two WC clusters serving children's zones (one near Group Therapy 0.08, one near therapy corridor 0.23-0.28). Recommended: Armitage Shanks Contour 21 Junior pan or equal. Update AR-40006 and AR-40007 (IPS panels). | WCH005 WC/toilet pan with seat & cover, 750 mm projection CANTILEVER, hospital pattern, rimless pan, vitreous china — listed in 0.05, 0.06, 0.09, 0.11, 0.22, 0.29, 0.30. BAS105 BASIN small general pattern in all ACC WCs. No paediatric pan or basin in schedule. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\40000_Schedules\11606-XX-ZZZ-SH-RHA-AR-40006- Sanitary Schedules.pdf | ARCH_DESIGNER | OPEN
M-102 | CRITICAL | MECHANICAL | VENTILATION_KITCHEN | Drg 1743_57_00 Ventilation Ground Floor + Mech Spec §11 | Kitchen (Room 0.31) extract design | IS EN 16282-7 (kitchen ventilation), CIBSE TM50, HBN 00-04, HSE/L8 (grease accumulation), TGD-B Section 3.4 (cooking-area ventilation) | Kitchen 0.31 is shown on Drg 57_00 with a single 250mm 360° disc-valve extract of only 114 L/s — equivalent to ~6 ACH for a 35m² kitchen. There is no canopy hood, no grease filter, no separate cooking-zone extract duct, no make-up air, no make-up balance with WCs, and no fire-rated kitchen extract ductwork. IS EN 16282-7 requires 700-900 m³/h per m² of cooking surface (≈300-400 L/s for even a small commercial kitchen). Without a canopy the kitchen will fail HBN 00-04, fail building control sign-off, and create smoke spread risk to dining 0.30. | Issue addendum confirming: (a) kitchen scope — is this a domestic-style preparation kitchen or commercial cooking? (b) If commercial, provide canopy + grease filtration + dedicated extract fan to IS EN 16282-7 + fire-rated stainless ductwork; (c) confirm capture velocity & make-up air strategy; (d) confirm interface with wet-chemical suppression (Ansul or equivalent) and BMS cause-and-effect with fire alarm. | Drg 57_00 ventilation schedule: 'E0031 Kitchen — Disc Valve 360° 250mm — 114 L/s' — no canopy / hood, no separate fan, no make-up air shown. Mech Spec contains no IS EN 16282-7 reference and no kitchen canopy specification. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_57_00.pdf | ME_DESIGNER | OPEN
M-104 | CRITICAL | MECHANICAL | VENTILATION_HEALTHCARE | Drg 1743_57_00 Ventilation schedules | Sensory room / Therapy room / Snoezelen ventilation rates | CIBSE Guide A Table 1.5 (10 L/s/person plus contaminant control), HBN 00-04 healthcare ventilation, BB101 (where applicable for paediatric users), HBN 26 (treatment rooms) | Sensory rooms 0.26, 0.27 (and Snoezelen) are shown on Drg 57_00 with supply 30 L/s @ NR<35 and 30 L/s extract via single disc valve. For a sensory room with 4-6 users + carers (typical CRC paediatric use) the CIBSE per-person minimum (10 L/s × 8 = 80 L/s) is not met. Therapy rooms (0.12, 0.10) show 30 L/s — again below minima for occupied therapy spaces. There is no demand-control CO2 sensor specified per room despite the variable occupancy profile, and no quiet-mode requirement (sensory rooms must be NR25 not NR35). | Reissue Drg 57_00 air change schedule with per-room CIBSE A and HBN 00-04 demonstration. Add CO2 demand sensor in each sensory & therapy room linked to MVHR via BMS. Specify NR25 acoustic limit for sensory rooms (not NR35) — re-select attenuators if required. | Drg 57_00 supply schedule rows S0021-S0027: '20 Activity / 26 Sensory / 27 Therapy — Disc Valve 360° 250 — 30 L/s — Max Noise <35'. Mech Spec §11.07 states 'Sound level NR35' as global figure. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_57_00.pdf | ME_DESIGNER | OPEN
M-106 | CRITICAL | MECHANICAL | DHW_LEGIONELLA | Drg 1743_53_00 + Mech Spec §9.03 + §10 | Domestic hot water — Legionella control | HSE L8 ACoP (Legionella), HTM 04-01 Parts A & B (water systems in healthcare), BS 8580, WHO Water Safety Plan | DHW heat-pump (Mitsubishi QAHV-N560YA, 40 kW, max flow temp 60°C) feeds a 200-litre stainless cylinder per Drg 53_00. No Legionella regime is specified: (i) no 60°C minimum storage stat setpoint, (ii) no weekly 65°C pasteurisation cycle programmed, (iii) no thermometer pockets shown at flow & return, (iv) HWS return circulating temperature requirement (≥55°C at every point) not stated, (v) no chlorine dioxide / Cu-Ag dosing or alternative supplementary control specified, (vi) no Written Scheme of Control or Responsible Person nomination per L8 §2.10. Heat-pump DHW at 60°C is borderline for Legionella control without an electric immersion heater pasteurisation cycle. | Issue addendum: (a) confirm Legionella Written Scheme of Control will be produced by Mech Contractor pre-handover per HSE L8 §2.10; (b) add immersion-heater pasteurisation cycle 65°C weekly to BMS strategy (BMS Drg 59_01); (c) add thermometer pockets at cylinder flow, secondary return, and most-distant outlet on Drg 53_00; (d) add commissioning requirement that secondary return reaches plant ≥55°C at all points; (e) confirm HTM 04-01 Part B sampling regime for first-year occupancy. | Drg 53_00 shows DHW heat-pump @ 60°C and 200L stainless cylinder but no L8/HTM 04-01 control measures, no pasteurisation cycle, no temperature monitoring points beyond cylinder stat. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_53_00.pdf | ME_DESIGNER | OPEN
S-008 | CRITICAL | C&S | COMPLIANCE | All structural drawings (11001 Foundation Plan, 11002 GF Plan, 11003 Roof Plan, 50001-50009, RC0000-RC0007) | Standard NOTES box (notes 3 and 7) on every sheet | I.S. EN 1997-1 + Irish NA (Geotechnical Design); I.S. EN 1990 (Basis of Design); BCAR SI 9/2014 Code of Practice (designer must verify ground-strata assumption against a GI report); TGD A1.1 (loadbearing elements must transfer loads safely to the ground). | Foundation design proceeds on the unverifiable assumption of 'undisturbed and firm soil' with no allowable bearing pressure stated and no Ground Investigation (GI) report referenced anywhere in the C&S pack. Any soft spots, made ground, or perched water at formation level will trigger an unbudgeted redesign (raft / piled solution), claims under PW-CF5 clause 10 (unforeseeable ground conditions), and programme slippage. For a CRC healthcare/day-care facility on a brownfield Swords site, ground conditions cannot be assumed. | Issue RFI to C&S designer to (a) attach the GI/site investigation report to the tender pack with named author, date, borehole/trial-pit log and laboratory schedule; (b) state characteristic and design bearing resistance (kN/m²) and reference Geotechnical Category (GC1/GC2/GC3) per EN 1997; (c) replace the blank 'soil stratum(a)' field in note 7 with the actual stratum identified in the GI; (d) confirm any chemical/sulphate testing for DS class to support concrete exposure selection. If no GI exists this must be commissioned before tender issue. | '7. Foundation formations to be in the following soil stratum(a) (see soil investigation report): _______Undisturbed and firm soil___________________________' | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\11001 - FOUNDATION PLAN.pdf | CS_DESIGNER | OPEN
S-100 | CRITICAL | C&S | DRAINAGE | Cl 2309 - SurfaceWaterAttenuation.xlsx + 12001 PROPOSED DRAINAGE | R41 calc; FMH/SW layout dwg 12001 | GDSDS Vol 2 §6 - permitted discharge for new developments in Greater Dublin = 2 l/s/ha or QBAR (greenfield), whichever is lesser; SI 9/2014 BCAR | Calc fixes max allowable discharge at 2 l/s (cell R41) but QBAR-greenfield for the 0.24 ha site = 1.36 l/s (R31). Designer has adopted 2 l/s without GDSDS / Fingal CoCo / Irish Water consent. If consent is granted only at 1.36 l/s (QBAR), the 75mm Hydrobrake orifice on dwg 12001 and the 96m³ attenuation volume are both under-designed; storage requirement rises to ~110m³ vs 98.7m³ provided — design fails GDSDS. | PM/CS_Designer to obtain written confirmation of permitted discharge rate from Fingal CoCo and/or Irish Water BEFORE TENDER; re-run attenuation calc and resize Hydrobrake at confirmed rate; if QBAR governs, increase coarse aggregate sub-base depth or add geocellular crate to demonstrate ≥10% spare capacity. | Max allowable discharge for the Site = 2 l/s ¦ QBAR for subject site based on site area of 0.2407 ha = 1.358 l/s ¦ Hydrobrake limited to 2 l/s | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Cl 2309 - SurfaceWaterAttenuation.xlsx | CS_DESIGNER | OPEN
S-101 | CRITICAL | C&S | DRAINAGE | 12001 PROPOSED DRAINAGE | Drawing 12001 — 'New SW pipe to council detail' note (top right) | GDSDS Vol 2 §3 — no new connections to combined sewers in Greater Dublin; Water Services Act 2007 §24 — pre-connection consent from Irish Water required; TGD H §2.4 | Drawing 12001 shows new SW discharge to 'existing manhole' / 'new manhole to council detail' with no statement whether downstream public sewer is separate-SW or combined. If combined, the connection is prohibited by GDSDS and Fingal CoCo will refuse Section 24 consent — drainage strategy invalid and CSA / tender pricing unreliable. | Issue RFI to Fingal CoCo confirming downstream sewer classification (combined vs separate SW); obtain Irish Water pre-connection enquiry response (PCE) and Connection Agreement; annotate drawing with sewer reference, IL and gradient at point of connection. | new manhole to council detail ¦ New concrete SW pipe to council detail | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\12001 - PROPOSED DRAINAGE.pdf | CS_DESIGNER | OPEN
X-001 | CRITICAL | FIRE/COORDINATION | COMPLIANCE | Fire Part B Compliance Report (ORS Doc 22481-Stage 2C) | Stage 2(c) Notes §12, §13, §14 | SI 496/2009 Building Control Regulations §11 (revised FSC trigger); SI 9/2014 BCAR — Code of Practice for Inspecting & Certifying Buildings and Works §3.2 (commencement notice / FSC linkage); TGD-B Vol 2 (2024) §B1 (means of escape) and §B3 (compartmentation) | The pack being tendered on 10-Jun-2026 contains DESIGN CHANGES (store under external stair, bin-to-bike store conversion, store/breakout reconfiguration in Activity Room 13) which the Senior Fire Prevention Officer Keith Boland confirmed on 08/04/2026 are NOT minor and REQUIRE a revised FSC and revised DAC under §11 SI 496/2009. The contract is therefore being procured against a design that the contractor cannot lawfully complete and occupy. Building cannot be opened until the revised FSC + DAC are obtained — a programme risk that crystallises as an Employer compensation event under PW-CF5 Clause 9.4 (instructed change / time extension) once the revision lands mid-construction. | Before tender issue: Employer's Representative (ER) to instruct ORS Fire and Rhatigan Architects to SUBMIT the revised FSC and revised DAC applications NOW so that grant dates can be tracked. Pack to include an explicit Information for Tenderers note stating: '(a) FSC dated 19/08/2025 governs at tender, (b) Revised FSC and DAC applications submitted [date] reference [BCMS no.], (c) Contractor to allow for and coordinate with grant of revised FSC/DAC prior to building occupation, (d) any consequential design refinement will be handled under PW-CF5 Clause 9 as Employer Change'. Without this, the Employer is procuring a contract it knows is not certifiable as drawn. | It was determined on 08/04/2026 following a formal response from SFPO Keith Boland that the works were not considered minor enough such that under Section 11 of SI 496 of the Building Control Regulations a revised FSC and DAC would be required for the above mentioned changes. … Please note commencement can still be issued on the basis of the existing granted FSC. However, the Revised FSC and DAC must be submitted an granted during the construction phase before the building is occupied. | Fire Part B Compliance Report (ORS Doc 22481-Stage 2C) | ER — Employer's Representative (Rhatigan & Co. acting as Lead Designer / coord.) | OPEN
X-002 | CRITICAL | FIRE/COORDINATION | COMPLIANCE | Architectural Wall & Partition Types AR-15001; Internal Door Schedule AR-40001; Ironmongery Schedule AR-40010; Fire Stopping Details AR-59001-59004 | WT1-WT6, WT-B1 to WT-B3, BO-1/BO-2 partition legend; door schedule fire rating column; ironmongery Sets 04, 06, 10A | TGD-B Vol 2 (2024) §B3 Internal Fire Spread (Structure) — Tables 3.1/3.2; FSC Condition 3 (compartment walls per TGD-B 2024 §3.5.5/§3.5.7/§3.5.9-3.5.14 + Appendix A); BS EN 1366 series (penetration seals); BS 9999:2017 §10.4 (compartmentation matrix to be shown on drawings) | Wall & Partition Types drawing AR-15001 lists WT1-WT6 and WT-B1 to WT-B3 with sound ratings but EVERY entry for fire rating reads 'Fire Rating: Refer to Fire Cert, Drawing No. 1000A, 1001A & 1002A' — the Fire Cert drawings are NOT included in this tender pack (ORS pack contains only 22481-PFD-XX-00-DR-F-003). Tenderers cannot price compartmentation construction. The bricklayer/plasterboard contractor must know whether a given WT-B1 blockwork run is 60-min, 30-min or non-rated. Compounded by the fact that the door schedule confirms only 4×FD30S + 1×FD60S (Fire Report Note 11) but ironmongery Sets 04/10A include 'Motorised door opener/closer with Magnetic locking device' on the kitchen FD60S — coordination of door + closer + hold-open device must be on a single Ironmongery + Door Type drawing or it will not survive site assembly. | Pre-tender (by 03-Jun-2026): Architect to (a) reissue AR-15001 with explicit fire rating against each WT/WT-B/BO partition type, (b) include the Fire Cert plans 1000A/1001A/1002A in the tender pack OR confirm they are superseded by AR-15001 fully marked-up, (c) cross-reference the 5 fire doors (D0.002 FILE & COMMS, D0.003 CLEANERS STORE, D0.009 KITCHEN, D0.014 STORE, D0.018 ACTIVITY ROOM STORE) to the matching compartment wall lines on AR-15001. Fire-stopping detail sheets AR-59001-59004 are numbered 1, 2, 3, 5 — Sheet 4 is missing from the pack; either reissue or confirm 'not used' on issue sheet. | WT2 Partition Wall Type 2 … Sound Insulation Rating: 50 RwdB Fire Rating: Refer to Fire Cert, Drawing No. 1000A, 1001A & 1002A. [repeated identically for WT1, WT3, WT4 in AR-15001] … Door D0.009 KITCHEN Set 04 FD60S [door schedule AR-40001] … Motorised door opener/closer with Magnetic locking device - fails to open on activation of fire alarm [ironmongery legend AR-40010] | Architectural Wall & Partition Types AR-15001; Internal Door Schedule AR-40001; Ironmongery Schedule AR-40010; Fire Stopping Details AR-59001-59004 | ARCH_DESIGNER — Rhatigan & Co. Architects (Lead Designer) | OPEN
X-004 | CRITICAL | FIRE/COORDINATION | COMPLIANCE | Mechanical Specification (T5) and Electrical Specification (T5); Arch Kitchen Layout AR-57012 Room 0.17 | FSC Condition 5; Mech Spec entire; Elec Spec §12; Arch Kitchen layout | FSC granted 19/08/2025 Condition 5 (kitchen suppression per IS EN 16282-7); IS EN 16282-7:2017 (kitchen ventilation — fire safety provisions for fixed fire-suppression systems); BS 6173 (gas appliances commercial); HTM 03-01 (specialised ventilation in healthcare premises) Annex on commercial kitchens | Grep of full Mechanical Specification returns ZERO hits for 'IS EN 16282', 'suppression', 'ansul' or 'kitchen hood' fire suppression. The kitchen serves a healthcare day-care centre (CRC Omni clients with disability) — Condition 5 of the granted FSC mandates a fixed suppression system to IS EN 16282-7 with interlocks to the gas supply, extract fan, fire alarm and (per ironmongery schedule) the FD60S kitchen door's magnetic hold-open device. None of these interlocks is specified — neither in the Mech Spec (extract + hood + supply gas), nor the Elec Spec (interlock wiring + alarm input), nor the Architectural Kitchen layout (mounting/access for the system). A bidder cannot price this scope. | Pre-tender (mandatory): ER to instruct T5 to issue a Kitchen Fire Suppression Specification section covering (a) fixed wet-chemical or equivalent system to IS EN 16282-7, (b) gas solenoid valve fail-closed on activation, (c) hood interlock to extract fan run-on then shutdown, (d) hard-wired signal to fire alarm panel, (e) release of mag-lock hold-open on the FD60S kitchen door (Set 04), (f) annual service regime to feed forward into HSE PCM O&M and HIQA inspection regime. Rhatigan to amend AR-57012 to show suppression bottle/cylinder location and access. Without this, the project fails FSC Condition 5 at first inspection. | FSC Condition 5 (per ORS Stage 2C Report) imposes IS EN 16282-7 kitchen suppression. Mechanical Specification full-text grep for '16282' returns 0 hits, for 'suppression' returns 0 hits, for 'kitchen hood' / 'ansul' returns 0 hits. Arch Kitchen Layout drawing AR-57012 shows extract hood symbol but no suppression annotation. Door D0.009 KITCHEN ironmongery Set 04 includes 'Motorised door opener/closer with Magnetic locking device - fails to open on activation of fire alarm' — interlock origin (kitchen suppression activation) not specified anywhere. | Mechanical Specification (T5) and Electrical Specification (T5); Arch Kitchen Layout AR-57012 Room 0.17 | ER — T5 Engineering (M&E) + Rhatigan Architects | OPEN
A-001 | HIGH | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Drawing Register | Section 15000 (Wall & Partition Types) and Section 17000 (Signage) | BS 1192 / BS EN ISO 19650-2 (CDE controlled-document numbering); RIAI Standard Conditions of Engagement (design info quality) | Two distinct drawings carry the same number 11606-XX-L00-DR-RHA-AR-17001 — one titled 'Wall & Partition Types', one titled 'Signage – Ground Floor'. CDE retrieval will return the wrong drawing. Contractor build risk: wrong document acted on. | Renumber Wall & Partition Types to 11606-XX-L00-DR-RHA-AR-15001 (consistent with Section 15000 numbering). Reissue register and reissue drawing under new number. Withdraw the duplicate-numbered version from CDE. | Register p.1: '15000 WALL & PARTITION TYPES — 11606-XX-L00-DR-RHA-AR-17001 Wall & Partition Types P08-S 1:100 A1' AND '17000 SIGNAGE — 11606-XX-L00-DR-RHA-AR-17001 Signage - Ground Floor P08-S 1:100 A1' | 11606-RG-RHA-AR-0001 Drawing Register p.1 | ARCH_DESIGNER | OPEN
A-002 | HIGH | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Drawing Register | Section 31000 Detail Wall Sections | BS 1192 / BS EN ISO 19650-2 | Drawing number 11606-XX-ZZZ-DR-RHA-AR-31001 is used for both 'Detail Wall Section - Sheet 1' AND 'Detail Wall Section - Sheet 2'. Ambiguity on CDE retrieval. | Renumber Sheet 2 to 31002. File inventory shows 31001, 31002, 31003 present in pack, so register entry is the error — correct the register. | Register p.1: '11606-XX-ZZZ-DR-RHA-AR-31001 Detail Wall Section - Sheet 1' and immediately below '11606-XX-ZZZ-DR-RHA-AR-31001 Detail Wall Section - Sheet 2'. | 11606-RG-RHA-AR-0001 Drawing Register p.1 | ARCH_DESIGNER | OPEN
A-003 | HIGH | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural pack delivery | Site Drawings (Section 10000), Room Layouts 60009/60029-60032, Details 51005/52001/53001-53002/55001/57001-57013/59001-59004, RCP 70001 | CWMF ARM4 (pack completeness for tender issue); SI 9/2014 (designer obligation) | Architectural register lists drawings 10004-10010 (Site Plan, Site Sections 1-6), 10014-10016 (Entrance details), 51005, 52001, 53001, 53002, 55001, 57001-57013, 59001-59004, 60009, 60029-60032, 70001 — but file inventory of the connected pack shows these NOT present. Register notes 'External works package to be issued by COB 22nd May' and 'Drawings to be issued by COB 21st May'. Today is 27-May-2026 — completeness unconfirmed. | Confirm status of external works package and outstanding drawings. If not issued, schedule date for issue. Pack cannot proceed to tender with drawings listed-but-not-present. | Register margin annotations: 'External works package to be issued by COB 22nd May' and 'Drawings to be issued by COB 21st May'. File inventory confirms absence. | 11606-RG-RHA-AR-0001 Drawing Register p.1-2 + pack manifest | ARCH_DESIGNER | OPEN
A-012 | HIGH | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section Q37 'Green/blue/biosolar roofs', clause 130 'Extensive green roof systems' | FSC Application FSC2513876FL Condition 7 (granted 19/08/2025): green roofs to comply with (i) BS 8616:2019 - Specification for performance parameters and test methods green roof substrates; (ii) Fire Performance of Green Roofs and Walls - DCLG UK: 2013; (iii) Green Roof Code of Best Practice UK: 2014. | Q37/130 names Bauder system but does not cite any of the three documents the granted FSC requires. Without these citations the Contractor's submittals will not be benchmarked against the FSC condition and Building Control are likely to refuse the Certificate of Compliance on Completion unless a revised FSC is granted in mitigation. | Insert at Q37/130/2 'Performance Standards' a new sub-clause: 'Substrate and system performance shall comply with BS 8616:2019. Fire performance and 500mm non-combustible firebreaks between PV arrays and vegetation shall comply with DCLG (UK) Fire Performance of Green Roofs and Walls 2013 and the Green Roof Code of Best Practice UK 2014. Contractor to submit third-party fire test reports for the proposed build-up.' Cross-reference Fire Cert Cond. 7. See F-005 for parent fire-side finding. | 130 Extensive green roof systems 1. Manufacturer: Bauder Ltd ... 1.2. Product reference: Bauder Extensive Sedum Blanket System ... 7. Vegetation: BauderGREEN SB Sedum Blanekt [no fire/BS 8616 references] | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.178 (Q37/130) | ARCH_DESIGNER | OPEN
A-013 | HIGH | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification (overall) | Sections L10, L20, L30, M50, M60, N10, N13, N14, P21 | TGD M (Access and Use) 2022; BS 8300-2:2018; NDA 'Building for Everyone' Booklets 2-5; Building Control (Amendment) Regulations 2014 - DAC requirements per SI 9/2014. | There is no consolidated Part M / BS 8300-2 / NDA compliance schedule in the Arch Spec. Aside from sanitary contrast notes in N13 and one BS 8300-2 reference in N14/270, the spec contains NO clauses for: hearing-loop induction systems, evacuation chairs and refuge spaces, accessible parking bay dimensions/markings, tactile/hazard warning paving, ramp gradients & landings, accessible counter heights, vision panels in doors, contrasting door leaf vs frame LRV, accessible signage tactile/Braille format. HIQA Day Centre registration and any DAC review will fail. Stage 2C is the gate at which these should be captured. | Add new section A45 'Accessibility & Inclusive Design Compliance Schedule' (or equivalent), cross-referencing each Part M requirement to the relevant Arch spec clause and to the DAC drawings. Items must include: induction loops (M&E coordination), refuge points (location per Fire Strategy), evacuation chair makes/locations, tactile paving to TGD M Diagram 1.18, parking bay layout to Diagram 1.9, accessible counter heights to BS 8300-2 §11. Issue with Tender Addendum. | [No clauses found for hearing loops, refuges, evacuation chairs, accessible parking, tactile paving, ramp gradients, accessible counters in the Architectural Works Specification - grep returns nil across all sections] | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf (whole document p.1-211) | ARCH_DESIGNER | OPEN
A-014 | HIGH | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section J40/710 Radon membrane (and elsewhere) | I.S. 10101:2020+A1:2024 National Wiring Rules (the correct Irish citation form). NSAI cataloguing convention: Irish-adopted European standard is 'I.S. EN [number]'; pure Irish standards take 'I.S. [number]'; BSI standards take 'BS' / 'BS EN'. | Project Brief flags that 'IS EN 10101' does not exist - the correct standard is I.S. 10101:2020+A1:2024 (National Rules for Electrical Installations). J40 cites 'IS EN 13967' (correct), L30 cites 'IS EN 942:2007' (correct), but the Fire Report Cond. 6 (page 4) twice cites 'I.S. 10101:2020+A1:2024' - the Arch Spec does not propagate the citation. PV-related arch clauses (roof under PV) and electrical co-ordination notes use loose phrasing. Consequences: tenderers price equipment to a non-existent standard, NSAI/BCAR audit logs the discrepancy as a Designer Defect. | Run full document audit: replace any 'IS EN 10101' (none found at present but inevitable in M&E spec) with 'I.S. 10101:2020+A1:2024'. Add a Standards Schedule at front of Architectural Spec listing every cited standard with its correct prefix and current edition/amendment. Cross-coordinate with M&E spec. | IS EN 13967 [J40] / IS EN 942:2007 [L30] - present uses are correct, but no master Standards Schedule exists. Fire Report Cond. 6 cites correctly: 'I.S. 10101:2020+A1:2024 National Rules for Electrical Installations'. | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.42 (J40), p.89 (L30); 22481-Stage 2C Report-Part B Compliance.pdf p.4 | ARCH_DESIGNER | OPEN
A-015 | HIGH | ARCHITECTURAL | COMPLIANCE | Internal Doors Schedule (drawing 40001) and Fire Strategy | Door D0.020 (Activity Room 0.20) and D0.018 (Activity Room 0.20) | TGD-B Vol.2 (2024) §3.5; FSC2513876FL grant condition record per Fire Report §11 (12/02/2026) - 4 no. FD30S (File & Comms, Cleaners Store, Store, Activity Room store) + 1 no. FD60S (Kitchen). | Door D0.020 (T1.1, room 0.20 Activity Room) has BLANK fire rating, BLANK fire-rating-acoustic-seals, BLANK control, BLANK comments columns in schedule 40001. Door D0.018 (T1.2, room 0.20 Activity Room) IS shown FD30S - but Fire Report references 'Store to 2 no. Activity Rooms' which is ambiguous if room 0.20 has two doors. Risk: contractor prices D0.020 as non-rated; on site the fire enclosure is compromised; BCAR Ancillary Cert cannot be signed. | Architect to confirm: (a) intent of D0.020 (non-rated final-exit type or store door); (b) fill all blank schedule columns; (c) reconcile against Fire Report Note 11 with a single 'Door-by-Door FSC Rating' tabulation cross-referenced to the Fire Strategy drawing. Issue clarification before tender close. | D0.020 T1.1 ACTIVITY ROOM 0.20 1000 2260 800mm Solid Hardwood, White Oak Laminate Colour 02 ... Set 09 [blank fire rating] [blank seals] Yes [blank] [blank] [blank] [blank comments] | 11606-XX-XXX-SH-RHA-AR-40001- Internal Doors Type Elevations & Schedule.pdf row 199 (D0.020) | ARCH_DESIGNER | OPEN
A-016 | HIGH | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Works Specification | Sections N13/331 (Sinks Type A), N13/331 (Sinks Type B), N13/331 (Sinks Type C) | BS 1192-2007+A2:2016 (controlled document principles); BS EN ISO 19650-2 §5.1.6 (Information Container identification); RIAI Standard Conditions of Engagement §5.2 'clarity of design instructions'. | Three different sink types are all numbered '331' in N13. A contractor reading the spec cannot reliably reference 'N13/331' in a tender clarification - the clause number is ambiguous. RFI and CE traceability will collapse during the JCT/PW-CF5 administration phase. | Renumber to N13/331, N13/332, N13/333 (and onwards) ensuring unique numbering. The 'Sink and Basin Combination' clause is currently labelled 332 - conflicts when 331 should have been 331/331A/331B. Re-issue spec with revision marker. | 331 Sinks Type A ... 331 Sinks Type B ... 331 Sinks Type C ... 332 Sink and Basin Combination ... 335 Washbasins ... 336 Washbasins ... 338 Washbasins | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.129-133 (N13) | ARCH_DESIGNER | OPEN
A-017 | HIGH | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section M50 - Flooring Types F1, F2, F3, F5 (Marmoleum) | HSE (UK) Slips & Trips Guidance HSG155; HSA Ireland Slip and Trip Hazards Guidance; HBN 00-10 Part B 'Floors' §3.6 (wet PTV ≥36); BS 7976-2 Pendulum Test Method. | Types F1/F2/F3/F5 cite slip resistance as 'DIN 51130 R9, PTV Dry ≥50' only - no wet pendulum value. Marmoleum in a Day Care environment is foreseeably contaminated (spillages, cleaning, incontinence). Without a specified PTV-Wet ≥36, slip-and-trip risk to vulnerable adults is not designed out. HIQA notifiable incidents and personal injury liability follow. | Add to M50/150 sub-clauses 1.4.1 for F1/F2/F3/F5: 'PTV Wet (slider 96) to BS 7976-2: ≥36 in all wet-foreseeable locations (entrance lobbies, accessible WCs, kitchen, dining, all therapy rooms). Where ≥36 cannot be achieved a textured safety vinyl to Type F4 specification (R11) shall be used.' Locate wet-zone flooring on a Floor Finishes Risk Plan. | Slip resistance value (SRV) (minimum)/ Pendulum test value (PTV) (minimum): DIN 51130 = R9., PVT Dry: =50, EN 13898: u =0.30. | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.111-115 (M50/150 F1, F2, F3, F5) | ARCH_DESIGNER | OPEN
A-018 | HIGH | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section L20 'Doors/shutters/hatches' | TGD M 2022 §1.3.3 Table 1.1 (effective clear width 800mm minimum to internal doors on accessible routes; 1000mm to principal doors; 1500mm to assembly room doors); BS 8300-2:2018 §6.4 Table 2. | L20 specifies door performance generically. The Internal Doors Schedule (40001) lists 800mm 'Ope' (which is opening size, not clear width). With a 44mm thick leaf and ironmongery (handle reach 65-100mm), a 800mm opening yields ~755mm effective clear width — below Part M 800mm minimum. Many doors are tagged 800mm in the Ope column. Contractor will fabricate to the figure and Part M fails at completion. | Amend L20 to add a new clause 'Effective Clear Width': 'Effective clear width of all doors shown in schedule 40001 to be measured at 90 degree open position from face of leaf to face of opposing stop, and shall be 800mm minimum on accessible routes, 1000mm on principal corridors, 1500mm on assembly room sets. Where schedule width is shown, this is the structural opening; door leaf width shall be sized to deliver clear width compliance.' Re-check schedule 40001 against TGD M effective clear width and update opening sizes upward where required. | [L20 contains performance clauses but no 'effective clear width' acceptance criterion. Schedule 40001 columns show 'Ope. Width' (e.g. 1000) and 'Ope' (800mm) without effective clear width verification] | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.83-88 (L20); 11606-XX-XXX-SH-RHA-AR-40001 (schedule) | ARCH_DESIGNER | OPEN
A-019 | HIGH | ARCHITECTURAL/COORDINATION | CONTRACT | Architectural Works Specification | Front matter (Document Control Sheet) and throughout | SI 9/2014 Building Control (Amendment) Regulations + Code of Practice for Inspecting and Certifying Buildings and Works §3.6 (Ancillary Certifier nomination); RIAI Standard Conditions of Engagement §3. | Spec contains no BCAR Ancillary Certifier allocation matrix and does not name designers for proprietary scopes (curtain walling, fire stopping, hoist, green roof, fall arrest, automatic doors all 'Contractor's choice / Submit proposals'). When the Assigned Certifier issues the Ancillary Certificate request, no Designer of record exists for these specialist sub-systems - leaving the Project Architect carrying residual design liability under the Code of Practice §3.6.4. | Insert a 'Designers and Ancillary Certifiers' table at front of spec listing each proprietary/specialist sub-system, the appointed designer, the relevant Ancillary Certifier signatory and certifier discipline (e.g. fire stopping = Specialist Sub-Contractor Designer with Chartered Fire Engineer counter-sign). Co-ordinate with Assigned Certifier register at Tender Stage. | All ironmongery: Manufacturer: Contractor's choice / Submit proposals. ... Fire-stopping system: Manufacturer: Contractor's choice / Product reference: Contractor's choice. ... Hoist - [no clause]. ... Automatic doors: Manufacturer: Submit proposals. | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf (multiple sections) | PSDP | OPEN
A-020 | HIGH | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section L20/480 (External aluminium doors) and L20/490 (Automatic sliding door) | TGD M 2022 §1.2.3 (level entry threshold ≤15mm with chamfered upstand ≤5mm vertical + chamfer); BS 8300-2:2018 §5.4.4 (max 15mm overall threshold height for accessible entrances, but for primary public entrance 0mm flush preferred). | L20/480 specifies 'thermally broken flush drained thresholds (14mm high) to be wheelchair friendly'. 14mm exceeds the 5mm sharp-edge limit and is at the absolute max of the 15mm guidance. Combined with carpet/floor finish make-up this is likely to exceed 15mm composite. Wheelchair users and trolley-borne service users will catch. HIQA observation finding likely. | Amend L20/480 to: 'Thresholds: thermally broken flush drained, maximum 5mm vertical upstand finished height above adjacent floor finish, with chamfer (max 1:2) to remainder. Where 5mm cannot be achieved, full ramped/recessed threshold detail to be issued as an Architectural Detail and co-ordinated with floor build-up.' For automatic sliding door L20/490 specify a zero-threshold compliant track set. | The doors are to have thermally broken flush drained thresholds (14mm high) to be wheelchair friendly. | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.84 (L20/480) | ARCH_DESIGNER | OPEN
A-021 | HIGH | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification (and Sanitary Schedule) | Section N13 (Sanitary), Room 0.06 C/P WC (Sanitary Schedule 40006) | Changing Places Consortium Technical Specification (2022) §2.1 minimum 12 m^2 room; §2.4 height-adjustable adult-size changing bench 1800mm length min; §2.5 ceiling track hoist with full XY coverage including over toilet and bench; §2.7 peninsular WC with 1000mm clear each side; BS 8300-2:2018 §18.5. | Spec clauses for adult changing bench (N13/488) and shower (N13/377) read 'Manufacturer: Submit proposals' with no Changing Places brand schedule. Sanitary schedule shows correct fittings but no Compliance Statement asserting that room 0.06 meets the Changing Places Consortium minimum technical specification (peninsular WC, 12 m^2 area, 1000mm each side, privacy screen, etc.). Without an explicit Changing Places compliance call-up, the Contractor will sub-optimise and HIQA registration as 'Day Service with Changing Places' may be refused. | Add new N13/488 sub-clause 'Compliance statement: Room 0.06 shall be configured, fitted out and commissioned to meet the Changing Places Consortium Technical Specification (current edition) in full. Contractor to submit compliance matrix prior to procurement.' Also include peninsular WC, privacy screen, height-adjustable basin, hoist (see A-010), and disposable paper roll dispenser to spec. Room Layout 60006 to carry Changing Places stamp. | 488 Adult changing units 1. Description: BNH900 - Changing Places 2. Manufacturer: Submit proposals 2.1. Product reference: Height adjustable changing bench, 3. Type: Height-adjustable 4. Size: 1800 mm length (minimum) | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.134 (N13/488); 11606-XX-ZZZ-SH-RHA-AR-40006 (sanitary) | ARCH_DESIGNER | OPEN
A-022 | HIGH | ARCHITECTURAL | OPERATIONAL | Architectural Works Specification (and Room Layouts) | Therapy Rooms 0.12, 0.21-0.29; Sensory Rooms 0.10, 0.27; WCs | HSE Estates 'Ligature Anchor Risk Assessment Guidance' (HSE Ireland 2018); HIQA Theme 5 Safe Services §5.4; National Standards for Residential Services for Adults with Disabilities §3.2 (suitability of premises for safe care). | Spec lists standard ironmongery (P21/610 round-pattern lever handles, P21/750 limiting door stays, L30 timber spindle balustrades) with no ligature-anchor-mitigation criteria for therapy/sensory/WC rooms used by service users with intellectual disabilities, autism, or self-harm risk. Although HIQA Day Services are not Mental Health Act-regulated, HIQA inspectors look for proportionate ligature-risk mitigation in adult-disability day-care environments. Risk: client incident, HIQA non-compliance. | Add a new section A55 'Anti-Ligature Strategy' identifying rooms (0.06 C/P WC, 0.05/0.09/0.11/0.22/0.29/0.30 Accessible WCs, sensory rooms, group therapy) requiring ligature-resistant ironmongery (sloped-top handles, anti-ligature door closers, hinged grab rails to released force), curtain track (already shown RAI902 anti-ligature in 0.04 Staff Shower - extend principle), and absence of overhead pipework. Co-ordinate with Service Brief / Clinical User Group. | 610 Lever handles 1. Description: To internal doors ... 4. Style: Round pattern [no anti-ligature criterion]. P21/750 Limiting door stays: 'Surface fix friction stay without hold-open' [protruding component]. | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.164 (P21/610, P21/750) | EMPLOYER | OPEN
A-104 | HIGH | ARCHITECTURAL | COMPLIANCE | C/P WC Door Schedule | Door D0.007, Room 0.06 | Changing Places Consortium 2019 §4.1 – min 950mm effective clear opening (outward opening); BS 8300-2:2018 Table 2 | D0.007 (C/P WC) scheduled as T1.2 single leaf, 1200 structural ope, '800mm' clear ope — Changing Places mandates 950mm clear. Adult wheelchair user with attendant and ceiling hoist transfer cannot pass through 800mm. Fails C/P certification. | Increase D0.007 to min 950mm clear ope (typically T1.2 structural ope 1100mm with 50mm frame allowance) and confirm outward opening with kick-down hold-open. Reissue Door Schedule 40001. | 40001 row D0.007: 'T1.2 C/P WC 0.06 1200 2260 800mm'. | 11606-XX-XXX-SH-RHA-AR-40001 | ARCH_DESIGNER | OPEN
A-105 | HIGH | ARCHITECTURAL | COMPLIANCE | Sanitary Schedule (Hoist HOI001) | Drawing 40006 + FF&E Totals 40008 | BS EN ISO 10535:2021 (mobile and fixed hoists); HTM 08-03 patient handling; HIQA Standard 5; CWMF tenderability (PW-CF5 BoQ pricing) | HOI001 specified as 'TRACK HOIST – ceiling mounted H style full coverage of space'. No make/model, no SWL, no track configuration, no charger position, no electrical interface, no structural pull-out load. Equipment vendor cannot price; structural engineer cannot design slab inserts. Major variation risk post-award. | Issue HOI001 datasheet addendum: nominate exemplar (e.g. Liko Likorall 250 + H-system) with SWL 250kg, full coverage track length [calc per room], gable-end traverse, ceiling fixing rated for static + dynamic load (kN), charger receptacle location coordinated on Elec drawings, IP rating, BS EN ISO 10535 cert. Cross-coord structural slab insert detail. | 40008 FF&E Totals HOI001: 'TRACK HOIST - ceiling mounted H style full coverage of space' — no make, no SWL, no track length, no charger. | 11606-XX-ZZZ-SH-RHA-AR-40006 + 40008 | ARCH_DESIGNER | OPEN
A-106 | HIGH | ARCHITECTURAL | COMPLIANCE | Reflected Ceiling Plan | Drawing 70001 — Room 0.06 C/P WC | Coordination: HOI001 ceiling hoist track must be shown on RCP for structural insert + bulkhead avoidance; HBN 00-09 finishes integrity; HTM 08-03 | RCP 70001 shows Room 0.06 with plain CEL02 ceiling and no track-overlay symbol, no bulkhead carve-out for charger, no clearance from sprinkler/light fittings. Installer will conflict with diffusers/lights at first-fix. Programme slip + re-routing cost. | Update RCP 70001 to overlay HOI001 track route (H-system) in Room 0.06, charger location, structural slab insert callouts, and clear 100mm offset zone from sprinklers/diffusers/luminaires. Add same overlay to all rooms with ceiling tracks (Therapy, C/P WC). | RCP 70001 Room 0.06 shows only 'C/P WC CEL02 (+2.735)' with no hoist track symbology. | 11606-45-L00-DR-RHA-AR-70001 | ARCH_DESIGNER | OPEN
A-108 | HIGH | ARCHITECTURAL | COMPLIANCE | Internal Finishes Schedule — Kitchen 0.17 | Drawing 40009 row 0.17 | BS 7976-2 / Pendulum Test Value (PTV); HSE / HSA slip-resistance guidance for commercial kitchens (R12 or PTV ≥36 in wet contaminated zones) | Kitchen floor specified F5 R10 (Forbo Safestep Aqua). For commercial kitchen with oil/water contamination R10 is borderline; R12 typically required. Slip-injury claim exposure and HSA inspection finding. | Upgrade kitchen floor finish to R12/PTV≥36 (e.g. Altro Stronghold 30 or Polysafe Verona PUR 4.5mm). Confirm with HSE Catering Specialist that selected finish suits the cleaning regime and chemical resistance. | 40009 row 0.17 Floor: 'F5 - 2.0mm Slip Resistant Vinyl Sheet, LRV 45%, R10 (Forbo Safestep Aqua, 180662 Reef Green)'. | 11606-XX-ZZZ-SH-RHA-AR-40009 | ARCH_DESIGNER | OPEN
A-109 | HIGH | ARCHITECTURAL | DOCUMENT_HYGIENE | Internal Finishes Schedule — Lobby 02 | Drawing 40009 row 0.38 | PW-CF5 tender completeness — every space must have defined ceiling finish for pricing | Lobby 02 (0.38) row has no Ceiling Finish, Door Frame, Architrave or Door Leaf entry (cells blank in the schedule). Lobby is on the staff egress route. Tenderer must price by assumption — leads to variation claim. | Populate row 0.38 in 40009 with same suite as Lobby 01 / Entrance Foyer (CEL02 moisture-resistant plasterboard, white sheen emulsion; Solid Hardwood White Oak frame/architrave; door leaf colour 02 or 03 as applicable). | 40009 row '0.38 LOBBY 02 ... F1 - 2.5mm Marbled Linoleum ... Coved skirting matched ... [BLANK ceiling/frame/architrave/leaf cells] ... N/A' window board. | 11606-XX-ZZZ-SH-RHA-AR-40009 | ARCH_DESIGNER | OPEN
A-111 | HIGH | ARCHITECTURAL | COMPLIANCE | Room Layout 0.10 Sensory Room | Drawing 60005..60010 area schedule | CRC Omni / HSE clinical brief — sensory rooms typically ≥10–12 m² for soft-play, projector throw, and wheelchair turn; BS 8300-2 1500mm wheelchair turn requires 2200×2200 manoeuvring area | Room 0.10 SENSORY ROOM is 6.76 m² — below typical CRC sensory standard. Wheelchair user with carer + sensory equipment (bubble tube, projector, soft mat) cannot occupy room safely. Risk of clinical brief non-conformity flagged at HIQA inspection. | Confirm with Employer/Client whether 6.76 m² complies with CRC Omni Day-Centre Schedule of Accommodation. If not, swap with adjacent room or remove equipment from scope. Either confirm by formal Employer instruction or rebrief. | 60010 plan: '0.10 SENSORY ROOM 6.76 m²'. | 11606-XX-L00-DR-RHA-AR-60010 | EMPLOYER | OPEN
A-112 | HIGH | ARCHITECTURAL | COMPLIANCE | Internal Doors Schedule | Drawing 40001 — Fire-rated door cross-reference | Fire Compliance Report Note 11 (4× FD30S to file/comms/cleaners/store; 1× FD60S to kitchen); TGD B Vol 2 2024 §3 + Appendix A | Door schedule contains 4× FD30S (D0.002 File & Comms, D0.003 Cleaners Store, D0.014 Store, D0.018 Activity Room 0.20). D0.018 ACTIVITY ROOM is rated FD30S but Fire Report does not identify Activity 0.20 as a place of special fire risk. Conversely Room 0.20 also has D0.020 (no rating shown). Mismatch between drawing schedule and Fire Cause-and-Effect; FSC condition compliance at risk. | Reconcile with Fire Engineer: (a) confirm whether Activity Room 0.20 is a sub-compartment per Fire Report (kitchenette + activity); (b) confirm D0.020 (Activity Room) rating intent (blank schedule cells = unpriceable); (c) reissue 40001 with reconciled FD ratings matched 1:1 to Fire Cause-and-Effect. | 40001 D0.018 'ACTIVITY ROOM 0.20 ... FD30S' AND D0.020 'ACTIVITY ROOM 0.20 ... [blank rating cell, blank ironmongery set 09, blank vision panel, blank hardware]'. | 11606-XX-XXX-SH-RHA-AR-40001 | ARCH_DESIGNER | OPEN
A-113 | HIGH | ARCHITECTURAL | DOCUMENT_HYGIENE | Internal Doors Schedule — D0.020 row | Drawing 40001 row D0.020 | PW-CF5 tenderability — every door row must define rating, ironmongery set, vision panel, hardware and notes | Row D0.020 (Activity Room 0.20) has 6 blank cells: FD rating column, Frame rating, Vision Panel Yes/No, BGU Yes/No, EN1125 Yes/No, Access Control note. Tenderer must guess — variation exposure. | Populate D0.020 with all standard data fields, confirm whether door is rated and self-closing, identify if it's a secondary egress door from Activity 0.20. | 40001 D0.020: 'T1.1 ACTIVITY ROOM 0.20 1000 2260 800mm Solid Hardwood, White Oak Laminate Colour 02 — Brown ... [blank] Set 09 [blank] [blank] Yes [blank] [blank] [blank] [blank] [blank]'. | 11606-XX-XXX-SH-RHA-AR-40001 | ARCH_DESIGNER | OPEN
A-114 | HIGH | ARCHITECTURAL | COMPLIANCE | Ironmongery & Access Control Schedule | Drawing 40010 — All Sets | IS EN 13637:2015 (electrically controlled exit systems); BS EN 1125 (panic), BS EN 179 (emergency exit), BS EN 1155 (electromagnetic hold-open), BS EN 1154 (closers), BS EN 1935 (hinges), BS EN 12209 (locks); TGD B Vol 2 §1.1 escape from special risk areas | Schedule 40010 lists Set 01–Set 16A with functional descriptors (mag lock, hold-open, fails to open) but cites NO BS/EN/IS product standards anywhere in the document. Mag-lock release on fire alarm (Set 04 Kitchen) must be IS EN 13637 — not certified by schedule wording. Tenderer cannot ensure compliant procurement. | Add product-standard column to 40010: each ironmongery item to cite EN/BS/IS standard (EN 1125 / EN 179 / EN 1154 / EN 1155 / EN 1935 / EN 12209 / EN 13637 / EN 1634-1 fire test). Add cause-and-effect matrix for mag-lock release on fire alarm and BGU. Specify maximum opening force ≤30N per TGD M. | 40010 Set 04 description: 'Motorised door opener/closer with Magnetic locking device - fails to open on activation of fire alarm' — no EN reference cited anywhere on the drawing. | 11606-XX-L00-SH-RHA-AR-40010 | ARCH_DESIGNER | OPEN
A-115 | HIGH | ARCHITECTURAL | COMPLIANCE | Stair Layout — Roof Access | Drawing 25001 — Stair 0.42 | TGD K 2014 §1.4 — max 16 risers per flight for general use; 36 risers for utility (roof access); BS EN ISO 14122-3 for industrial steps; OSH/HSA Working at Height Regs 2006 | Stair 0.42 has 24 risers in a single straight flight (1 to 24 shown continuously) with one intermediate 'landing' but no dimensional break. If categorised as 'general access' this exceeds TGD K 16-riser limit. If 'maintenance only' it must be locked-off, signposted, restricted. Drawing does not declare use-classification. | Add note to 25001 declaring stair as either (a) general access (then redesign with intermediate landing every ≤16 risers) or (b) maintenance/utility roof-access only with signage, key-restricted door XD0.023, fall-arrest anchor at top, and exclusion from accessible escape route. Cross-coordinate with Fire Engineer (roof not an escape level). | 25001 plan: '0.42 STAIR 24 9.85 m²' with continuous numbering 1–24 risers and single 'landing' note at riser 15. | 11606-44-L00-DR-RHA-AR-25001 | ARCH_DESIGNER | OPEN
A-118 | HIGH | ARCHITECTURAL | DOCUMENT_HYGIENE | Fire Stopping Details — missing Sheet 4 | Drawings 59001/59002/59003/59004 | TGD B Vol 2 §3 compartmentation continuity; ASFP Blue Book; fire-stopping installer chain-of-evidence | Pack contains Fire Stopping Sheets 1, 2, 3, and 5 — Sheet 4 absent. Standard set is sequential. Sheet 4 typically covers cable trays/bus-bars/ductwork penetrations. Without it, the fire-stopping contractor lacks the typical service-penetration details for one whole category; risk of either non-compliant ad-hoc detailing on site or RFI clarifying which service penetrations are covered. | Issue Sheet 4 (or formally re-number existing sheets 1-2-3-4 and update Drawing Register to remove Sheet 5 gap). Confirm Sheet 4 scope intent before tender close. | 50000_Details folder listing: '59001 Sheet 1', '59002 Sheet 2', '59003 Sheet 3', '59004 Sheet 5' — no Sheet 4 present. | 11606-XX-ZZZ-DR-RHA-AR-59001/02/03/04 | ARCH_DESIGNER | OPEN
E-001 | HIGH | ELECTRICAL | FSC Condition Compliance | Electrical Specification + drawings | FSC Condition 2 - Fire detection standard cited as 'IS 3218 - Latest Edition' and 'IS 3218: 2013', not 'IS 3218:2024' as required by granted condition | Granted FSC Condition 2; I.S. 3218:2024; SI 9/2014 BCAR Assigned Cert obligation to comply with granted FSC. | Non-compliance with granted FSC condition. BCAR Assigned Certifier cannot sign off. Tender pricing will be based on 2013 edition, which has materially different requirements (zoning, cause-and-effect, IP-based panel security, manufacturer declaration format). Re-tender or substantial post-tender variation likely. | Issue tender addendum: replace every 'IS 3218 - Latest Edition' and 'IS 3218: 2013' with 'I.S. 3218:2024' explicitly. Add explicit clause requiring manufacturer's written confirmation of compliance with I.S. 3218:2024 specifically. Add cause-and-effect matrix submittal (see E-002). | Spec §12.01: 'The fire alarm system shall fully comply with the recommendations I.S 3218 latest edition'. Spec §12.02: 'shall receive written confirmation from the selected equipment manufacturer that the proposed scheme is in full compliance with I.S 3218: 2013'. Bill item 68-01: 'Complete supply, installation and testing of new Fire Alarm System to IS 3218' (undated). FSC Condition 2 (granted 19/08/2025): 'The fire detection and alarm system to comply with IS:3218:2024'. | Spec: §4.00, §5.00, §6.00, §7.00, §8.00, §10.00, §10.10, §12.00, §12.01, §12.02, §13.00, Bill 68-01 ¦ Drawings: 1743_68(00), 1743_68(01) | EE_DESIGNER | OPEN
E-002 | HIGH | ELECTRICAL | FSC Condition Compliance / I.S. 3218:202 | Electrical Specification + drawings | No cause-and-effect matrix included or required of tenderer - mandatory under I.S. 3218:2024 | I.S. 3218:2024 §6 (system design - cause and effect required for L1/L2/L3 systems); FSC Condition 2; HBN 00-01; AOV interlock per TGD-B 2024. | Tenderers price ambiguous system behaviour. Different fire alarm sub-contractors will price different C&E logic. Access control 15-second time delay (per Fire report) needs explicit C&E entry. AOV smoke vent isolation (Spec §12.14 says 'NOT nuisance trip due to General Fire Alarm') needs explicit mapping. Door maglock release on alarm needs explicit mapping. Plant shutdown sequences (kitchen suppression interlock per FSC Condition 5) need mapping. Risk of evacuation failure or false trips post-handover. | Issue tender addendum including a draft cause-and-effect matrix as Engineer's design intent. Require tenderer to develop, submit and have approved a full C&E matrix prior to commissioning, signed off by competent fire alarm engineer to I.S. 3218:2024. Bill item to be added. | Spec §12.08 'Sequence of Operation' states only: 'Upon activation of any manual call point or automatic sensor in the development the system shall automatically switch all sounders to give a continuous (evacuate) audible alarm only, and (where applicable) mechanical plant shut down shall be activated and plant shut off or door unlock signals generated if required.' Spec §12.10 lists interface targets ('Alarm Communicator, Relevant door access system, Lift, AOV systems, BMS MCC panels and Equip') but provides no matrix, no trigger-to-action mapping, no per-zone behaviour. Fire report Note 9 (16/09/2025) records cause-and-effect for access control agreed in principle 'based on the principals of IS EN 13637 2015' but no full system C&E matrix exists in the tender pack. | Spec: §12.08, §12.10, §12.14 ¦ Drawings: 1743_68(00), 1743_69(03), 1743_69(04) | EE_DESIGNER | OPEN
E-003 | HIGH | ELECTRICAL | Regulatory Citation / Wrong Jurisdiction | Electrical Specification + drawings | Spec cites 'BS 7671:2018' as primary wiring rules - WRONG JURISDICTION; should be I.S. 10101:2020+A1:2024 (project brief explicitly flagged this) | I.S. 10101:2020+A1:2024 is the National Rules for Electrical Installations in Ireland (statutory). BS 7671 is the equivalent for the UK and has no legal standing in Ireland. The 'IEE' was renamed to 'IET' in 2006 - this is a 20-year-old citation. The '16th Edition' was superseded in 2008 (17th), then 2018 (18th); referencing it is over 17 years out of date even in the UK. 'ETCI' rules were replaced by NSAI I.S. 10101 in 2020. | Tenderers may price to wrong standard. Certifier (RECI/Safe-Electric) Completion Certificate under SI 220/2019 ECSSA must be to I.S. 10101:2020+A1:2024. BCAR Assigned Cert non-compliance. Insurance and warranty issues. | Issue tender addendum: delete all BS 7671 references; delete all 'IEE 16th Edition' references; replace with 'I.S. 10101:2020 + Amendment 1:2024' throughout. Update §2.05, §7.01, §8.02, §8.07, §10.04, §12.16, §13.02 specifically. | Spec §2.05 Standards lists: 'BS 7671:2018, Requirements for Electrical Installations, including amendments.' alongside 'IS 10101 Wiring Rules by NSAI'. Spec §7.01: 'The sub-contractor shall undertake to effectively earth the whole of the electrical installation in accordance with the 16th Edition of the IEE wiring regulations'. Spec §8.07 'Wiring to Fixed Equipment' uses '16th Edition of IEE wiring regulations'. Spec §10.04 and §12.16 reference 'I.E.E. Current Edition'. Spec §8.02 references 'ETCI 10101 - latest edition'. PV §13.02 references 'Electro Technical Council of Ireland (E.T.C.I.) latest edition'. | Spec: §2.05, §7.01, §8.02, §8.07, §10.04, §12.16, §13.02 ¦ Drawings: All electrical drawings - check title-block standard references | EE_DESIGNER | OPEN
E-004 | HIGH | ELECTRICAL | Regulatory Citation / Wrong Jurisdiction | Electrical Specification + drawings | Emergency lighting standard cited as 'I.S. 3217: 2013 latest edition' (contradictory) - current is I.S. 3217:2023 | I.S. 3217:2023 is the current Irish emergency lighting standard. The '2013' version has been withdrawn. The combined phrase 'I.S. 3217: 2013 latest edition' is self-contradictory. | Tenderers price to obsolete standard. 2023 edition has different requirements for high-risk task area lighting, duration in healthcare premises, ATS test protocols, signage luminance, and uniformity. Risk of post-handover failure to comply with statutory periodic test requirements per HBN 00-01 and FSC compliance. | Issue tender addendum: replace 'I.S. 3217: 2013 latest edition' with 'I.S. 3217:2023' explicitly. Replace 'IS3217 - Latest Edition' with 'I.S. 3217:2023' throughout (8 sections). Specify in spec: emergency lighting duration 3-hour confirmed for healthcare day-care use (already stated §10.10 but tie to I.S. 3217:2023 §6.3). Re-confirm ATS testing per I.S./EN 62034:2012+A1:2023. | Spec §10.10 Emergency Lighting Installation - General: 'The sub-contractor shall be responsible for the, supply, installation and commissioning of a complete emergency lighting system in accordance with I.S. 3217: 2013 latest edition.' Throughout spec (§4.00, §5.00, §6.00, §7.00, §8.00, §10.00, §12.00, §13.00): 'IS3217 - Latest Edition.' Spec §10.13: 'Ensure that I.S 3217: 2013 is complied with and issue a certificate of compliance to state this.' | Spec: §4.00, §5.00, §6.00, §7.00, §8.00, §10.00, §10.10, §10.12, §10.13, §12.00, §13.00 ¦ Drawings: 1743_63(01) Emergency Lighting | EE_DESIGNER | OPEN
E-005 | HIGH | ELECTRICAL | Scope vs FSC Condition / Project Hygiene | Electrical Specification + drawings | FSC Condition 5 'Lock Stop' kitchen knock-off switch not specified in Electrical spec or bill - mandated by granted FSC for deep-fat frying suppression interlock | Granted FSC Condition 5; I.S. EN 16282-7 (commercial kitchen ventilation/fire suppression); I.S. 10101:2020+A1:2024 §537 (emergency switching). | Granted FSC condition will not be met at completion. BCAR Assigned Cert blocked. Tender pricing missing - tenderers will not allow for: Lock Stop emergency switching device (red mushroom-head latching switch at escape route), contactor with shunt trip in kitchen final circuits, gas solenoid valve interlock, fire alarm cause-and-effect entry for kitchen suppression activation, suppression system relay-to-fire-alarm interface. Likely £3-8k variation post-tender. | Issue tender addendum: add new electrical section 12.24 'Kitchen Lock Stop Switch and Suppression Interlock' specifying: (a) Lock Stop emergency latching switch (BS EN 60947-5-5 / I.S. 10101 §537), located on route of escape outside kitchen, labelled per Condition 5; (b) shunt-trip contactor on kitchen final circuit; (c) gas solenoid valve 24V interlock (coordinate with Mech); (d) fire alarm relay interface (suppression activation auto-trips electrical + gas via fire panel); (e) auto restart inhibit until manual reset. Add bill items 68-18 'Kitchen Lock Stop and Suppression Interlock' and amend 62-10 to include kitchen plant. | FSC Condition 5: 'A suitably located "Lock Stop" (electrical knock off) switch is to be provided for manually isolating any gas and electrical supply in the kitchen area (switch to be located on route of escape). Maintenance testing and inspection details are to be recorded on the fire safety register.' Electrical spec contains ZERO references to 'Lock Stop', 'kitchen interlock', 'gas isolation', 'deep fat fryer', or 'kitchen suppression interlock'. Confirmed via grep: 'kitchen' appears only twice in the spec, both in project description (§2.01) and §11 of fire door listing - no electrical interlock requirement. | Spec: §2.01, §2.03, §12 (missing section) ¦ Drawings: 1743_62(00) General Elec - Kitchen 0.17, 1743_69(00) MDB Schematic | EE_DESIGNER | OPEN
E-006 | HIGH | ELECTRICAL | FSC Condition Compliance / PV | Electrical Specification + drawings | PV section (13.0) does not implement FSC Condition 6 sub-clauses (a) firebreak, (b) signage, (c) cables - text paraphrased incorrectly with typos ('NFDA 1' vs 'NFPA 1'; 'Section 11.2' vs '11.12') | Granted FSC Condition 6 (a), (b), (c); RC62 Recommendations for Fire Safety with PV; NFPA 1 §11.12; MCS Guide; I.S. 10101:2020+A1:2024 §712 (Solar PV); BS EN 62446-1 commissioning. | Granted FSC condition not met. Fire-fighter risk (no clear DC isolation strategy). BCAR non-compliance. Tender pricing inadequate. Also conflicts with Architectural F-003 finding on roof PV scope ambiguity. | Issue tender addendum rewriting §13.0: (1) correct typos to 'NFPA 1 Section 11.12'; (2) add 500mm firebreak per Condition 6(a) - coordinate with green roof per Condition 7; (3) signage per Condition 6(b) at main entrance, at meter, at array, at inverter, at any battery storage, in compliance with I.S. 10101:2020+A1:2024 §712.537.4 and RC62 §6; (4) cables Condition 6(c) - solar DC cable to TUV 2 PfG 1169 or equivalent; (5) firefighter switch at building entrance (NOT 'similar to HV discharge lighting' - this is wrong); (6) DC isolators at array per I.S. 10101 §712.537.2.2; (7) AC isolator at inverter and at main board; (8) Type II SPD on DC and AC sides; (9) RCD Type B if transformerless inverter (already noted Solis-3P 12K-4G - confirm); (10) Lightning Protection coordination per BS EN 62305 (see E-007); (11) MCS installer certification; (12) BS EN 62446-1 commissioning certificate. Confirm bill item missing (no PV bill line exists - see E-018). | Spec §13.0 preamble: 'NFDA 1 (Fire Code) Section 11.2 for PV Systems.' [SHOULD BE 'NFPA 1 Section 11.12']. Spec §13.0: 'The roof covering/deck under the PV panels will be of non-combustible construction.' but does NOT specify the 500mm firebreak between arrays and any green roof per FSC Condition 6(a). 'Signage will be provided within the entrance area at ground floor level advising of the presence of PV system installation.' but does not specify content/placement per FSC Condition 6(b) ('at access level and at the location of the PVS arrays, inverter and battery storage to inform responding Fire Service Personnel, in accordance with I.S. 10101:2020+A1:2024'). FSC Condition 6 references I.S. 10101:2020+A1:2024 explicitly; spec §13.02 uses obsolete 'E.T.C.I. latest edition'. PV isolation §13.0: 'The PV system shall include an isolation switch similar to that required for high voltage discharge lighting' - WRONG REFERENCE; PV requires firefighter-accessible AC isolator (RC62) plus rooftop DC isolators per I.S. 10101 §712. | Spec: §13.0, §13.02 through §13.13 ¦ Drawings: 1743_60(00) Site Electrical, 1743_69(00)/(01) MDB Schematic, Architectural Roof Plan 11606-XX-ZZZ-DR-RHA-AR-11002 | EE_DESIGNER | OPEN
E-007 | HIGH | ELECTRICAL | Project Hygiene / Gross Cut-Paste Error | Electrical Specification + drawings | Lightning Protection section §12.20 describes a different project: 'School Type Building located at Convent Hill, Ballina, Co. Mayo' - 2-storey building, wrong site | BS EN 62305-2 (Lightning Protection Risk Assessment) requires accurate building geometry, occupancy class, services, structural type as inputs. A risk assessment based on wrong inputs is invalid. HTM 06-01 healthcare resilience requires demonstrated LPL. | (a) Tenderers cannot price properly - building is single-storey not 2-storey; (b) Risk assessment by Specialist Contractor would be invalid; (c) PV array LPS coordination per FSC Condition 6 cannot be confirmed; (d) Confidence-undermining for all reviewers - if this section is cut-pasted from another project, what else might be? (e) Bill item 68-12 mislabels: 'Complete supply, installation and testing of Lightning Protection System as indicated on the drawings including interfacing them with the Fire Alarm.' - LPS does not interface with FA. Suggests this is also boilerplate-paste. | Issue tender addendum: rewrite §12.20 from scratch for THIS project - single storey, 57 Rathbeale Road Swords, K67 EP62, healthcare day-care centre occupancy class, building L x W x H per Arch GA, structural type per Structural spec, roof construction with PV per Arch Roof Plan 11606-XX-ZZZ-DR-RHA-AR-11002, services entering/leaving per Site Plan. Require BS EN 62305-2 risk assessment to determine required Protection Level (I, II, III or IV - cannot be pre-determined as 'Level 3' without RA per current §12.20). Coordinate LPS earth with PV array bonding and main equipotential bonding earth. Fix bill item 68-12 label. | Spec §12.20 Lightning Protection System: 'General Building Outline Details are as follows: - School Type Building located at Convent Hill, Ballina, Co. Mayo. - New Build Concrete and Steel Structure over 2 levels. - Ground / 1st + Roof Over. - Highest Point of Building above Ground Level _ 11.0 m - Street Level to Highest Roof Point - It is Noted that the Roof Structure is of a Steel Construction.' The actual project (per Fire report and Arch GA) is a SINGLE-STOREY day-care centre at 57 Rathbeale Road, Swords, Co. Dublin K67 EP62, 867m² gross internal area. | Spec: §12.20, Bill 68-12 ¦ Drawings: 1743_60(00), Architectural Roof Plan, 1743_69(00) | EE_DESIGNER | OPEN
E-008 | HIGH | ELECTRICAL | Project Hygiene / Wrong Project Content | Electrical Specification + drawings | Spec contains extensive 'School Lighting Notes (Primary & Secondary)' (§10.17) and 'classroom' bill items - this is a healthcare day services centre, not a school | Project brief identifies the building as a healthcare day-care centre (HSE / CRC Omni Unit 48A). Applicable lighting standard is CIBSE LG2 (Lighting in Healthcare Premises), not Department of Education TGD 033 / school lighting. EV TGD reference should be TGD-L Buildings Other Than Dwellings or the HSE EV policy. | Wrong lighting design intent - tenderers may install school-grade controls (key switches, teacher wall override, classroom PIR settings 300 lux at 700mm, corridor 5-minute timeout) instead of healthcare (LG2 lux levels, tunable white for sensory rooms, CRI Ra>90 in clinical areas, dementia-friendly lighting). Wrong EV reference. Wrong cable spec (apartments). Suggests entire spec is a cut-paste from a school project - confidence in all other sections undermined. Inappropriate bill items create scope disputes. | Issue tender addendum: (1) DELETE §10.17 in entirety; (2) REPLACE with new section §10.17 'Healthcare Lighting Notes' per CIBSE LG2:2023, EN 12464-1:2021, HTM 06-01, HBN 00-01 with: lux levels per room type (therapy room 300 lux, sensory room dimmable 100-500 lux tunable white, group therapy 300 lux, treatment 500 lux, kitchen 500 lux, corridor 150 lux, accessible WC 200 lux, plant room 200 lux, external 30 lux at entrance), CRI Ra>80 (Ra>90 in any clinical examination space), glare UGR<19 in therapy/work, dementia/dignity considerations, lighting controls accessible to wheelchair users, PIR override capability, DALI scene presets for sensory rooms; (3) Rewrite §5.04 deleting 'apartments' reference; (4) Rewrite §11 EV reference replacing 'TGD 033 School Building Projects' with TGD-L (Buildings Other Than Dwellings) 2022 + HSE EV Standards (if any); (5) Rewrite induction loop labels from 'SEN Base - Class Base 1/2' to actual room names per Arch GA (Group Therapy Room, Activity Room, Hall, Reception); (6) Fix bill items 62-12 ('induction loops in classrooms' -> '...in Hall, Group Therapy Rooms, Reception'), 62-14 ('classroom trunking' -> 'perimeter trunking in therapy/activity rooms'), 62-09 (DELETE - no existing school). | Spec §10.17 'School Lighting Notes (Primary & Secondary)' (44 lines covering classrooms, teaching walls, teaching desks, school PE Hall, 'Principal/Caretaker' key switches, '16 classroom schools and over', school commissioning certs). Spec §11 EV: 'Electric Vehicle Charging (EVC) is to be installed in accordance with the 2nd Edition TGD 033 School Building Projects and Compliance with Part L of the Building Regulations.' Bill 62-12: 'Induction loop systems in classrooms and GP Hall'. Bill 62-14: 'classroom trunking system'. Bill 62-09: 'fibre links between existing school and new extension data cabinets'. Induction loop §12.22 systems labelled 'SEN Base - Class Base 1', 'SEN Base - Class Base 2', 'SEN Base - Central Activity Space'. Spec §5.04 (Flat Twin & Three Core PVC): 'This shall be the specification of the cable to be used within the apartments.' | Spec: §5.04, §10.17, §11.0, §12.22 System 2/3/4, Bill 62-09, 62-12, 62-14 ¦ Drawings: 1743_63(00) Lighting, 1743_60(00) Site Electrical | EE_DESIGNER | OPEN
E-009 | HIGH | ELECTRICAL | Accessibility / BS 8300-2 §18.6 / TGD M | Electrical Specification + drawings | Disabled WC alarm pull cord, reset and remote indicator not specified despite multiple accessible WCs - bill item present (68-11 / duplicated 68-13) but no technical specification | BS 8300-2:2018 §18.6 (Accessible WC emergency assistance alarm); TGD M 2022 §3.3; I.S. 10101:2020+A1:2024 §537. | Statutory accessibility non-compliance for healthcare premises. DAC application risk (project brief noted F-007 DAC status uncertain). Pricing scope ambiguity - tenderers may price refuge system (irrelevant for single-storey) or omit WC alarms entirely. Multiple accessible WCs across pack each need: red pull cord 800-1100mm above floor reaching to within 100mm of floor, contrasting colour, ceiling-mounted red alarm beacon visible outside cubicle, audible sounder, reset button INSIDE WC at 800-1100mm AFFL, illuminated repeater outside WC, alarm signal to reception/staff base. | Issue tender addendum: (a) DELETE duplicate Bill 68-13 (also see E-019); (b) RENAME Bill 68-11 to 'Accessible WC Emergency Assistance Alarm System per BS 8300-2:2018 §18.6'; (c) add new spec section 12.24 detailing system per BS 8300-2 §18.6 - pull cord assembly, ceiling indicator, reset button, remote indicator at reception, audible signal, no fire alarm interface (do NOT route through fire panel as bill 68-11/13 wrongly states); (d) confirm number of accessible WCs per Arch (count from AR-60005, -60009, -60011, -60022, -60029, -60030); (e) consider whether any space is designated refuge - if not (single-storey), remove 'Refuge' wording from bill item. | Bill items 68-11 and 68-13 (DUPLICATED LINE): 'Complete supply, installation and testing of Disabled Refuge System as indicated on the drawings including interfacing them with the Fire Alarm.' No technical specification for disabled WC alarm pull cord exists in the spec body - grep on 'pull cord', 'WC alarm', 'accessible WC', 'disabled WC' returns zero hits in 5,928-line spec text. Bill 68-11/68-13 use the term 'Disabled Refuge System' which is a different system (refuge alarm at protected stair landings for evacuation comms with mobility-impaired) - the building is single-storey so refuge is unlikely to apply. Arch pack has multiple Accessible WCs (AR-60005, AR-60009, AR-60011, AR-60022, AR-60029, AR-60030). | Spec: §12 (missing section), Bill 68-11, Bill 68-13 (duplicate) ¦ Drawings: 1743_62(00) General Elec, 1743_68(00) Protective Services, AR-60005, AR-60009, AR-60011, AR-60022, AR-60029, AR-60030 | EE_DESIGNER | OPEN
E-010 | HIGH | ELECTRICAL | Healthcare Resilience / HTM 06-01 | Electrical Specification + drawings | No surge protection (SPD), AFDD, or healthcare resilience strategy specified per HTM 06-01 / I.S. 10101 §443 / §722 / §532 | I.S. 10101:2020+A1:2024 §443 (Protection against transient overvoltages - SPD requirement mandatory for buildings with PV and lightning protection); §443.4 (AFDD - mandatory consideration for premises with sleeping accommodation, healthcare); §722 (Vehicle charging - already specified); HTM 06-01 (Electrical Services Supply and Distribution Healthcare); HBN 00-01. | I.S. 10101 §443 non-compliance for buildings with PV and LPS (both planned). Higher equipment failure risk from transients (especially with DALI controls, BMS, fire alarm IP networks, CCTV NVR). Risk of fire from arc faults. RECI/Safe-Electric Completion Certificate will be flagged. Healthcare resilience not assessed - if any clinical equipment (oxygen concentrators, treatment devices in therapy rooms, lift) requires uninterruptible supply, post-handover variation likely. | Issue tender addendum: (1) Add §4.23 'Surge Protection' specifying Type 1+2 combined SPD at main intake (PV+LPS site = mandatory), Type 2 SPD at sub-boards serving sensitive electronics (data, fire alarm, BMS, DALI), Type 3 SPD at point-of-use for critical equipment; (2) Add §4.24 'AFDD' requiring AFDD/MCBO consideration per I.S. 10101 §443.4 for sleeping/healthcare loads (provisional sum); (3) Add healthcare resilience risk assessment requirement - confirm with HSE Brief whether HTM 06-01 Grade A/B/C applies and whether standby generation required for kitchen, comms, lifts, life safety; (4) Confirm Section 9 'Standby Generator: Not Applicable' is correct decision based on HSE clinical risk assessment - documented justification required for BCAR file; (5) Bill items required. | grep on 'surge', 'SPD', 'AFDD', 'arc fault', 'HTM' across spec body: ZERO hits. Spec §4 Mains Distribution describes MCCB main breaker, fault level 50kA, TN-S earthing - but no Type 1/Type 2 SPD requirement at main board. No AFDD requirement for therapy rooms/sleeping accommodation as per I.S. 10101 §443.4. No HTM 06-01 / HTM 06-02 healthcare resilience reference. No UPS for life-safety systems beyond fire alarm 48hr battery (§12.04) and CCTV UPS (§12.19). No mention of standby generator (Section 9 'Not Applicable to this project') with no rationale - HTM 06-01 considers risk-based standby for healthcare. | Spec: §4 (missing §4.23/§4.24), §9.1, §10.17 ¦ Drawings: 1743_69(00) MDB Schematic, 1743_69(01) SDB Schematic | EE_DESIGNER | OPEN
E-011 | HIGH | ELECTRICAL | Project Hygiene / Wrong Architect Named | Electrical Specification + drawings | Health & Safety section §14.02 names 'Simon J Kelly (SJK) Architects' as Project Supervisor Design Stage - actual architect is Rhatigan Architects (RHA) | Safety, Health and Welfare at Work (Construction) Regulations 2013 (SI 291/2013) Article 4 (PSDP appointment in writing). Spec also incorrectly cites 'Health Safety and Welfare at Work (Construction) regulations 1995' (§14.05) and 'S.I. 44 of 1993' (§14.05) and 'Health & Safety at Work Act 1974' (§3.38) and 'Safety Health & Welfare at Work Act 1989' (§14.02) - all superseded by 2005 Act and 2013 Construction Regs. | Statutory PSDP/PSCS responsibility unclear. Construction Regulations 2013 (SI 291/2013) requires named PSDP for design stage - if SJK is named in tender but RHA is the actual PSDP, contract documents conflict with statutory appointment letters. Confidence-undermining - if architect identity is wrong, what other project particulars are wrong (see E-007 wrong site, E-008 school content)? | Issue tender addendum: rewrite §14 in entirety to reflect (a) correct PSDP (confirm with HSE - likely Rhatigan Architects or a dedicated PSDP); (b) correct PSCS (confirm with QS prelims); (c) replace ALL 1995/1989/1974 H&S Act references with: Safety Health and Welfare at Work Act 2005 + Safety Health and Welfare at Work (Construction) Regulations 2013 (SI 291/2013) + General Application Regulations 2007 (SI 299/2007); (d) replace 'European Council Directive 92/57/EEC' reference with citing the transposing Irish regs; (e) replace 'S.I. 44 of 1993' (Schedule 1) reference. | Spec §14.02 Health and Safety: 'The client has appointed Simon J Kelly (SJK) Architects as Project Supervisor for the design Stage of the project to carry out on the duties set out in Article 4 of the Regulations.' Fire report repeatedly references 'Rhatigan Architects' (e.g. Stage 2(b) Note 4: 'This alteration was discussed and agreed with Rhatigan Architects'). Architectural drawing series 11606-XX-* file naming convention (RHA) confirms Rhatigan as Architect of Record. | Spec: §3.38, §14.02, §14.04, §14.05 | EE_DESIGNER | OPEN
E-018 | HIGH | ELECTRICAL | Bill of Quantities / Tender Document Int | Electrical Specification + drawings | Tender Summary missing bill items for Section 11 EV Charging, Section 13 PV system, Section 12.20 Lightning Protection (mis-labelled), Section 12.21 Aspirating Detection, Section 12.22 Induction Loops, and Section 12.23 Staff Attack | PW-CF5 Contract requires complete priced Bill at tender. Public Spending Code / OGP procurement guidance - bill must reflect scope. Missing items = post-tender variations = procurement audit issue. | Tenderers will (a) leave items unpriced; or (b) bury costs in 'M-10 Other Item ?'; or (c) submit qualifications. Post-tender variations inevitable. HSE budget integrity compromised. Tenders will not be directly comparable - bid evaluation invalid. | Issue tender addendum adding to MAIN SUMMARY: '8. Sub-Total for (66) EV Charging Installation'; '9. Sub-Total for (67) PV Installation'; '10. Sub-Total for (69) Lightning Protection'. Create new bill detail pages for sections 66, 67, 69. Reword bill 68-12 to remove 'interfacing with Fire Alarm' (LPS doesn't interface). Add explicit nurse call bill if scope is real (clarify with HSE - §12.23 reference to Schrack may be a cut-paste from another spec). Add bill for Kitchen Lock Stop (see E-005). Add bill for SPD (see E-010). Also fix VAT rates: spec shows '21%' but standard Irish VAT is 23% since 2014. | MAIN SUMMARY OF TENDER (final page) lists only sub-totals for: (M) Misc; (62) General Service; (63) Lighting & Emergency Lighting; (64) Containment; (65) BMS Mech Plant Controls & Power; (68) Fire Alarm System Installation. NO line for: Section 11 EV Charging (spec describes dual outlet charger plus ducting); Section 13 PV (26no panels, inverter, ballast, commissioning); Section 12.20 Lightning Protection appears under (68) Fire Alarm System as bill 68-12 (mis-categorised - LPS is not fire alarm); Section 12.22 Induction Loops captured only under bill 62-12 (described as 'classrooms and GP Hall'); Section 12.23 Staff Attack captured under bill 68-09 but vague; Section 12.21 Aspirating Detection captured under 68-15 (correct location but very vague); no nurse call bill despite §12.23 referencing Schrack Seconet nurse call integration. | Spec: Bill items 62, 63, 64, 65, 68, MAIN SUMMARY OF TENDER, FORM OF TENDER VAT | EE_DESIGNER | OPEN
E-105 | HIGH | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Drawing 1743_63-01 + Spec §10.10 to §10.13 | Emergency Lighting | I.S. 3217:2023 (Emergency Lighting — current edition); I.S. EN 1838; I.S. EN 62034 | Drawing 1743_63-01 cites 'IS 3217 - 2013' in luminaire data blocks ('FULLY COMPLIANT WITH IS 3217:2013-A1:2017'); spec §10.10 also references 'I.S. 3217: 2013'. I.S. 3217:2023 has been current since 2023 — supersedes the 2013+A1:2017 edition. Cited 'BS 5266 part 7 LG12' is UK guidance. New requirements in 2023 include: higher minimum lux on escape routes (1 lux floor average increased to 1 lux minimum at any point), additional task-area illumination at refuges/disabled WCs, defined illumination of fire alarm panels and accessible WC alarms, anti-panic open-area lighting performance. Risk: emergency lighting designed to 2013 will under-light at FSC sign-off and require re-design/re-spec at install stage. | Re-issue spec §10.10–10.13 and update drawing 1743_63-01 luminaire data plates to I.S. 3217:2023. Verify: (1) min 1 lux at any point on escape route centre line, (2) min 0.5 lux on open-area floor, (3) emergency lighting at fire alarm panel and AOV control panel ≥ 5 lux, (4) refuge/disabled WC luminaire wattage uplift, (5) high-risk task lighting in kitchen ≥ 15 lux at hob. | Drawing 1743_63-01 luminaire schedule: 'FULLY COMPLIANT WITH I.S./E.N. 60598-2-22, I.S./E.N. 60598-1, I.S./E.N. 62034 + A1=2018, I.S./E.N. 50171, THE EVD, THE EMC, THE RoHS AND THE BATTERY EUROPEAN DIRECTIVES'; spec §10.10 'a complete emergency lighting system in accordance with I.S. 3217: 2013 latest edition' | 1743_63-01.pdf; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-106 | HIGH | ELECTRICAL | DESIGN_INCOMPLETE | Drawing 1743_69(00) — MDB Schematic | Main Distribution Board incomer | I.S. 10101:2020+A1:2024 §433.1 Discrimination; §534 SPDs; HTM 06-01 §6.27 Healthcare LV resilience | MDB schematic shows 200A 4P+N MCCB incomer with downstream feeders (SDB1, SDB2, MCC01, multiple ASHP feeders, EV charger, PV) but: (a) no documented short-circuit & discrimination study (selectivity between 200A MCCB and 40A/50A/63A downstream MCBs not demonstrated), (b) Surge Protective Device (SPD) referenced as 'BOARD TO INCORPORATE SURGE PROTECTION' in text annotation but no SPD type (Type 1+2 vs Type 2), Iimp (kA 10/350) or Up (V) specified, (c) no spare-way capacity declared (industry minimum 20%), (d) no phase-balance schedule shown — heat-pump compressors and EV likely single-phase loaded heavily. Risk: nuisance tripping in service; uncoordinated tripping during a fault takes whole building dark; loss of essential mechanical heating/cooling for vulnerable users; lightning-induced surge could destroy PV inverter, fire panel and IT infrastructure simultaneously. | (1) Issue full discrimination study at tender — required by §433.1 and contractor cannot price without it. (2) Specify SPD as Type 1+2 combined, Iimp ≥ 12.5 kA per pole (10/350 µs), Up ≤ 1.5 kV, with separate Type 2 SPDs in each SDB and at PV AC isolator and EV charger. (3) Declare phase-balance schedule with circuit loadings per phase. (4) Confirm minimum 20% spare ways at MDB and each SDB. | Drawing 1743_69(00) 'BOARD TO INCORPORATE SURGE PROTECTION' [annotation only — no SPD specification]; 'MAIN BOARD TO INCORPORATE SURGE PROTECTION' repeated on MDB. No discrimination chart, no phase loading schedule, no spare-way percentage shown. | 1743_69_00.pdf; 1743_69_01.pdf | EE_DESIGNER | OPEN
E-107 | HIGH | ELECTRICAL | DESIGN_INCOMPLETE | Drawing 1743_68(00) Protective Services + Spec §12.02 | Fire detection grade | I.S. 3218:2024 §6 Categories; HTM 05-03 / FSC Cond 2 | Drawing 1743_68(00) annotation states 'L2/L3 fire detection and alarm system' for the day-care. I.S. 3218:2024 grades are L1 (full coverage), L2 (escape routes + rooms opening onto them + high-risk areas), L3 (escape routes only), L4 (escape routes only with smoke only), L5 (designed). Stating 'L2/L3' is contradictory and unbiddable. For a healthcare day-care occupied by vulnerable adults with intellectual disability, L1 should be considered — particularly given dependence on staff to assist evacuation. Spec §12.02 repeats 'L2/L3'. FSC Cond 2 granted on basis of fire strategy — must match strategy category. Risk: under-detection of fire in unoccupied rooms (stores, plant); contractor priced cheaper L3 then HSE/CRC require L1 at handover. | Confirm with Fire Engineer (cross-ref F-001 to F-008) the specific I.S. 3218:2024 category. For CRC day-care with intellectual-disability service users, recommend L1 to all rooms and voids >800mm, with heat detectors in kitchen and store rooms and beam detection if any tall lobby. Re-issue spec §12.02 and drawing 1743_68(00) annotation with unambiguous single category. Include cause-and-effect matrix as Appendix. | Drawing 1743_68(00) note: 'The overall building will be provided with an L2/L3 fire detection and alarm system with smoke detectors in the stairs and heat detectors with built-in sounders in each room all in accordance with I.S 3218 latest edition'; spec §12.02 identical wording. Note also 'stairs' — building is single-storey, no stairs. | 1743_68_00.pdf; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-108 | HIGH | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Drawing 1743_69(03) + Spec §12.22 | Disabled refuge / EVC + Accessible WC Alarm | BS 8300-2:2018 §18.6 (disabled refuge & WC alarms); I.S. EN 81-76 (refuge protocols); TGD M 2010 | Drawing 1743_69(03) shows 'EVC EMERGENCY VOICE COMMUNICATION SYSTEM/DISABLED REFUGE INTERCOM' and 'DISABLED ALARM SYSTEM SCHEMATIC' as indicative only ('EXACT WIRING DETAILS TO BE CONFIRMED BY MANUFACTURER / SPECIALIST'). For a single-storey day-care there is debate whether disabled refuge is required (refuges are escape-stair-pressurised lobbies); however ACCESSIBLE WC ALARMS in every WC are mandatory per BS 8300-2 §18.6. Spec does not mandate: pull-cord at 1.0m AFFL within 100mm of door + 100mm from floor, red bangle, reset at WC, indicator AND audible signal outside WC, summary indicator at reception, monitored connection to fire panel (per HSE/CRC standard). Schematic shows 10-zone controller in reception but no audible-visual outside WC, no labelling rules, no spec of cord type or compliance with BS 8300-2. Risk: post-handover replacement of all WC alarms to meet TGD M / BS 8300 compliance — significant rework in finished accessible WCs. | Re-issue spec §12.22+ with full BS 8300-2 §18.6 accessible WC alarm requirements: pull-cord configuration, audio-visual outside WC (red flashing beacon + sounder), summary indicator at reception, reset at WC only, monitored 24V loop. Confirm whether disabled refuge required (single-storey + protected route = generally no) — if yes, install EN 81-76 compliant 2-way intercom with handsfree at refuge + master at fire alarm panel. Add ironmongery cross-ref to architect for compliance with door egress under power loss. | Drawing 1743_69(03) 'DISABLED ALARM SYSTEM SCHEMATIC' shows '10 ZONE CALL CONTROLLER LOCATED AT RECEPTION' with 'reset' and 'mute' but no outside-WC indicator, no pull-cord spec, no reset rules; 'INDICATIVE SCHEMATIC - FOR LOCATIONS OF TOILET ALARM SYSTEMS - REFER TO 68 SERIES DRAWINGS'; spec contains no §18.6 BS 8300-2 compliance clauses. | 1743_69_03.pdf; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-109 | HIGH | ELECTRICAL | DESIGN_INCOMPLETE | Drawing 1743_62(00) + Spec §10.1 | Lighting design — therapy + sensory rooms | CIBSE LG7 / SLL Code for Lighting; CIBSE LG2 (Hospitals & Healthcare); IES TM-30 colour fidelity | Drawing 1743_62(00) shows 8 luminaire types (A through H) — all are standard 4000K downlights, spotlights, feature lights and IP66 wall lights — no tunable-white, no RGB, no high-CRI healthcare-specified fittings. For a CRC day-care: (a) Sensory Room R0.18 requires dimmable 50–500 lx + RGB + tunable white + variable speed mood control — drawing shows only standard downlight 'A_23W_3,000lm_LED down light (dali) Ø230mm', (b) Therapy Rooms R0.12, R0.13, R0.21, R0.25 to R0.31 require 300–500 lx variable colour temperature for sensory regulation, not fixed 4000K, (c) Activity Room R0.15 needs >500 lx with diffused glare control (UGR <19) for craft and visual tasks, (d) Kitchen R0.10 needs 750 lx at hob and tamper-resistant IP54 fittings at prep area. CRI/Rf not specified — healthcare requires Rf ≥85, R9 ≥0 (red rendition for skin tone observation). No lighting design calculations included. | Issue full CIBSE LG7+LG2 lighting calculations per room as Appendix to spec. For sensory room R0.18 specify tunable white 2700K–6500K + RGB controllable via touch panel, dimmable 0.1%–100%. For therapy rooms specify tunable white 3000K–5000K, dimmable, CRI ≥90, R9 ≥50. Kitchen hob luminaire IP54 above-prep, 750 lx. Specify Rf ≥85 minimum (TM-30) and UGR <19 to all occupied rooms. Re-issue luminaire schedule on 1743_62(00) with healthcare-grade specification. | Drawing 1743_62(00) lists luminaire types A–H — all standard 4000K LED, no tunable-white or RGB called out; spec §10.1 'Item / Description: A_23w_3,000lm_Led down light (dali) Ø230mm... no mention of colour temperature, CRI/Rf, tunable white, sensory room special requirement' | 1743_62_00.pdf; 1743_63_00.pdf; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-110 | HIGH | ELECTRICAL | DESIGN_INCOMPLETE | Drawing 1743_69(00) + Spec §11.0 | EV charging provision | I.S. 10101:2020+A1:2024 §722; SEAI EV grant criteria; TGD-L 2nd Ed 2022; Mode 3 IEC 61851 | Drawing 1743_69(00) shows 'CAR CHARGER UNIT SUPPLIED AND INSTALLED INCLUDING LOAD MONITORING / INFRASTRUCTURE ONLY FOR FUTURE FIT-OUT OF CAR CHARGER UNITS' — single dual-outlet charger plus ducting. Spec §11.0 says 7kW dual but configured to deliver 3.6kW. Issues: (a) for HSE healthcare day-care expecting 25+ staff and visitor traffic, 3.6kW (slow charging) is below current TGD-L requirement, (b) Type B RCD required at EV charger (cross-ref E-102) not stated, (c) Open Charge Point Protocol (OCPP 1.6 / 2.0) compliance referenced but not Open Smart Charging Protocol (OSCP) which is now required for HSE estate via SEAI Public Sector framework, (d) no specification of accessible bay charger (TGD-M reach 850–1100mm AFFL — drawing does not confirm), (e) no separate metering for billing — public-sector EV chargers must have MID-approved separate meters which spec does reference but not shown on MDB schematic, (f) load monitoring system not specified — required to prevent overload of 200A incomer. | Confirm with Client EV charging strategy (2× 22kW vs 1× 7kW dual). Specify Type B RCD at EV charger (or built-in 6mA DC detection per IEC 62752). Add OSCP compliance to spec. Confirm accessible bay arrangement (TGD-M reach + 1200mm transfer zone). Specify dynamic load management with MID-approved sub-metering. Cross-reference to architects' carpark layout drawings. | Drawing 1743_69(00) 'CAR CHARGER UNIT SUPPLIED AND INSTALLED INCLUDING LOAD MONITORING / INFRASTRUCTURE ONLY FOR FUTURE FIT-OUT OF CAR CHARGER UNITS'; spec §11.0 'The dual outlet charger shall be capable of delivering 7 kW (32amp) configured to deliver at 3.6 kW.' | 1743_69_00.pdf; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-111 | HIGH | ELECTRICAL | DESIGN_INCOMPLETE | Drawing 1743_62(01) Roof + Spec §13.0 | PV array — 18 panels 333W = 6kWp | I.S. EN 62446 (PV system documentation); IEC 61730 (PV safety); RC62 + NFPA 1 §11.12 (cited in spec); I.S. 10101:2020+A1:2024 §712 PV | Drawing 1743_62(01) shows 18 PV panels at 333W (6kWp) feeding a 3-phase inverter. Spec §13.04 describes 26× SOLARWATT 400/405/410W panels and §13.05 specifies a Solis 12kW 3-phase inverter (12kWp inverter for 6kWp array — over-sized inverter, will inverter operate below MPPT range). Issues: (a) array size discrepancy 18 vs 26 panels and 333W vs 405W = ~6.0kWp drawing vs 10.5kWp spec, (b) Solis 12kW inverter is significantly over-sized for either array — wastes capex and reduces inverter efficiency, (c) DC isolator location not stated (must be at array per IEC 62446), (d) AC isolator at incomer not shown — required by ESB Networks NC6 connection rules, (e) ESB Networks NC6 connection application not mentioned, (f) Firefighter switch / PV emergency disconnect at exterior wall not shown on any drawing (RC62 §3 requirement, FSC Cond 6), (g) NFPA 1 is US standard — should be I.S. EN 50438 or IEC 62116 for grid protection, (h) 500mm firebreak from any green roof not stated (cross-ref to architect green-roof design). | Reconcile array size between drawings and spec — issue revised PV array layout with confirmed panel count, Wp per panel, total kWp. Select inverter sized 100–110% of array kWp. Specify: DC isolator at array (lockable, IP65), AC isolator within 1m of meter cabinet (firefighter switch), 500mm firebreak signage at array, ESB Networks NC6 application included by contractor, monitoring portal compatible with HSE energy reporting. Replace NFPA 1 reference with I.S. EN 50438 / IEC 62116. Cross-ref to FSC Cond 6 evidencing. | Drawing 1743_62(01) shows '18 PV PANELS', 'PV INVERTER' panel; drawing 1743_69(00) shows '9+9 = 18 PV PANELS 333W EACH / PHOTO-VOLTAIC ARRAY INSTALLATION AND CABLING BY SPECIALIST – 18 PANELS – OUTPUT OF 6 kW'; spec §13.04 '26no SOLARWATT Classic H2.0 Pure Glass Foil Module', spec §13.05 'Solis-3P 12K-4G 3000 inverter'; spec §13.0 cites 'NFDA 1 (Fire Code) Section 11.2 for PV Systems' [misspelled — should be NFPA 1, but NFPA is US standard not applicable in IE] | 1743_62_01.pdf; 1743_69_00.pdf; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-112 | HIGH | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Electrical Specification | §5.13 Fire Alarm Cabling / §12.06 | I.S. 3218:2024 §16 cable types; I.S. EN 50200 / I.S. EN 50575 CPR | Spec §5.13 specifies 'FP Plus Enhanced' (UK Prysmian brand) rated to BS 5839 part 2 fire test (UK code). Should reference I.S. 3218:2024 enhanced fire-resisting cable per I.S. EN 50200 PH120, with CPR class B2ca-s1a, d0, a1 (per Construction Products Regulation 305/2011 mandatory from 2017 in Ireland). 'BS 5839 part 2' has been superseded — current is BS 5839-1:2017 in UK but in Ireland the standard is I.S. 3218:2024. Spec §12.06 names 'Morley Apollo' as the fire-alarm panel/detector — Morley is now end-of-life on most panel ranges; should be open-protocol Apollo / Hochiki / Notifier. Risk: contractor specifies UK-brand obsolete equipment and fails CPR marking inspection at handover. | Replace 'FP Plus Enhanced' with: 'Enhanced fire-resisting cable to I.S. EN 50200 PH120 (e.g. Prysmian FP200 Gold, Drogheda Cables Firecel SR/114E or equal & approved), with CPR class B2ca-s1a,d0,a1 per Reg (EU) 305/2011.' Update spec §12.06 panel reference to 'open-protocol addressable analogue panel (e.g. Hochiki Latitude, Advanced MxPro 5, Apollo Discovery or equal & approved)'. Verify all referenced cable standards are CPR-compliant. | §5.13 'The fire alarm cabling shall be wired exclusively in FP Plus Enhanced or equivalent rated for 2 hours having an overall red LSF sheathing'; §12.02 'The system shall be open protocol as manufactured by Morley Apollo or equivalent' | Electrical Specification .pdf | EE_DESIGNER | OPEN
F-001 | HIGH | FIRE | COMPLIANCE | Fire Part B Compliance Report (22481-Stage 2C) | Notes 1a vs Condition 4 (p.3) | TGD-B Vol 1 2024 vs TGD-B 2006 Reprint 2020 | Compliance report was completed in accordance with 'TGD-B V1 2024' (Note 1a). However Condition 4 of the granted FSC requires concealed spaces (cavities) to be in accordance with 'Section 3.3 of Technical Guidance Document Part B 2006 (Reprint 2020)'. Two TGD-B versions in the same fire compliance package. Tenderer scope of standards unclear. | Clarify in Fire Strategy report which TGD-B version applies to which element. Reissue Fire Strategy clarification or addendum. Confirm tenderer uses TGD-B 2024 for primary compliance and TGD-B 2006 Reprint 2020 only for cavity barriers per the FSC condition. | Note 1a: 'A compliance report completed in accordance with TGD-B V1 2024.' Condition 4: 'Concealed Spaces (Cavities) shall be in accordance with Section 3.3 of Technical Guidance Document Part B 2006 (Reprint 2020).' | 22481-Stage 2C Report p.1, p.3 | PSDP | OPEN
F-002 | HIGH | FIRE | COMPLIANCE | Fire Part B Compliance Report | Note 9 (p.4) — Access control cause and effect | IS EN 13637:2015 (electrically controlled exit systems); IS 3218:2024 (fire detection cause-and-effect) | Note 9 states 'Cause and effect of access control proposal reviewed and agreed based on the principals of IS EN 13637 2015... Types of systems and ironmongery are yet to be approved.' Tenderer is being asked to price ironmongery/access control with the specification still open. Variation exposure on award. | Either (a) freeze ironmongery and access control specification before tender issue and incorporate into Arch ironmongery schedule (AR-40010), OR (b) issue performance specification with provisional sum and a clear protocol for selection post-award. | Fire Report Note 9: 'Types of systems and ironmongery are yet to be approved. Design team meeting held on the 16/09/2025.' | 22481-Stage 2C Report p.4 | ARCH_DESIGNER | OPEN
F-003 | HIGH | FIRE | COMPLIANCE | FSC Condition 6 — Photovoltaic System | Fire Report Condition 6 (p.3-4) | FSC Condition 6; IS 10101:2020+A1:2024; RC62; NFPA 1 §11.12; MCS/ECA guidance; PV roof spec | FSC Condition 6 imposes specific PV system requirements (RC62, NFPA 1, MCS, IS 10101:2020+A1:2024, 500mm firebreak between PV array and green roof, non-combustible roof covering under PV, signage at access level, weather-resistant cables). However NO PV system appears in the drawing inventory reviewed so far — neither in Arch RCP, nor in Elec drawings 60-69 series. Either PV is included but undocumented, or PV is omitted despite being a granted FSC condition. | Confirm PV scope: (a) if PV is included, ensure all 4 standards are referenced in M&E spec and that Arch roof construction supports PV array per Condition 6 sub-clauses (a)/(b)/(c). (b) if PV is omitted, formally request amendment to granted FSC to remove Condition 6. | Fire Report Condition 6: 'Where PV panels are provided, it is the responsibility of the specialist contractor to ensure that the Photovoltaic Systems have been installed correctly...' (full condition references RC62, NFPA 1 §11.12, MCS/ECA, IS 10101:2020+A1:2024). | 22481-Stage 2C Report p.3-4 | ME_DESIGNER | OPEN
F-007 | HIGH | FIRE | CONTRACT | Pack scope | DAC status | Disability Access Certificate per Part 3 Building Control Regulations 1997-2024; TGD-M; BS 8300-2:2018 | Per Fire Report Note 14, a REVISED DAC is required following the 31/03/2026 design changes. Original DAC status not stated in this pack. Tenderer cannot confirm whether DAC is granted, pending, or to-be-applied-for. | State DAC status explicitly in tender pack preliminaries. Confirm application number, grant date, conditions if granted. Confirm revised DAC submission timeline. | Fire Report Note 14: '...a revised FSC and DAC would be required for the above mentioned changes.' No DAC information elsewhere in pack. | 22481-Stage 2C Report p.5 | ARCH_DESIGNER | OPEN
H-004 | HIGH | HEALTHCARE | SAFEGUARDING_OBSERVATION | 11606-XX-L00-DR-RHA-AR-11001 GA Plan + AR-40001 Internal Doors + AR-57009 Therapy Rooms | All 1:1 therapy rooms 0.12, 0.23, 0.24, 0.25, 0.26, 0.28 and Meeting & Consultation 0.32 | Children First Act 2015 §11 (organisations providing 'relevant service' must have safeguarding measures); HIQA National Standards for Children's Residential Services — Theme 1 (Child-Centred Services) Standard 1.6: 'spaces designed to allow appropriate observation while preserving dignity'; HSE Safeguarding Vulnerable Persons at Risk of Abuse policy; CRC operational risk management. | None of the 1:1 therapy rooms (0.12, 0.23, 0.24, 0.25, 0.26, 0.28) shows a glazed observation panel to the corridor on the GA plan, the Door Schedule AR-40001 or the room layouts AR-57009. Each room hosts one therapist alone with one child for 30–60 min sessions. This is a core Children First Act safeguarding failure — single-adult-with-child rooms in a children's disability service must have either (i) a vision panel to a circulation space, OR (ii) an internal CCTV with consent protocol. The current door specification (laminate door leaves with no vision panel called out) creates uninspected 1:1 contact — Tusla and HIQA WILL raise this as a Significant Risk on first inspection. | ARCH_DESIGNER to add minimum 300×900 mm vision panel (laminated safety glass, optional manual privacy blind controlled by exterior side) to ALL 1:1 therapy room doors (D0.015, D0.021–D0.025, D0.029, D0.033 Meeting & Consultation). Cross-ref Door Schedule AR-40001 and Ironmongery Set 10A which currently covers therapy rooms with no vision panel. Update specification clause for glazing as fire-rated where door is on a protected route. | GA Plan 11001: Therapy Rooms 0.12, 0.23, 0.24, 0.25, 0.26, 0.28 shown with solid doors and no observation glazing to Corridor 02 / Corridor 01. Door schedule AR-40001 lists laminate leaves with no vision panel. Ironmongery Set 10A applies to D0.021–D0.029 with no glazing reference. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\50000_Details\11606-76-XXX-DR-RHA-AR-57009- Furniture Details - 0.23, 0.24, 0.25, 0.26 & 0.28 Therapy Room.pdf | ARCH_DESIGNER | OPEN
H-005 | HIGH | HEALTHCARE | SENSORY_ROOM_OPERATIONAL_BRIEF | 11606-XX-L00-DR-RHA-AR-11001 GA Plan | Sensory Rooms 0.10 (6.76 m²) and 0.27 (10.06 m²) | HBN 11-02 Common Activity Spaces §4.7 (sensory integration); BB93 'Acoustic design of schools' Annex A (SEN therapy spaces); ISNA/Snoezelen guidance — Multi-Sensory Environment minimum 12–15 m² to permit vestibular swing arc + ball pool + projection wall; HTM 08-01 acoustic isolation NR ≤25. | Sensory Room 0.10 at 6.76 m² is approximately half of the minimum 12–15 m² required for a functional Multi-Sensory Environment / sensory integration room. The OT cannot install a ceiling-anchored vestibular swing (requires ~3.0 m clear arc), nor a ball pool with transfer space, nor projection wall + floor mat zone simultaneously. Sensory Room 0.27 at 10.06 m² is also under-sized. No ceiling track anchor, no acoustic panel specification, no tunable lighting (RGB + tunable white per HBN/best practice) is scheduled for either room. Reception of a child with sensory processing difficulty in an under-specified room can be actively counter-therapeutic and may trigger dysregulation incidents. | EMPLOYER + ARCH_DESIGNER to confirm sensory integration brief with CRC clinical lead OT. Re-evaluate room sizes against MSE protocol — recommend 0.10 expanded to ≥12 m² by absorbing adjacent ACC WC 0.09 or 0.11. Add to specification: (a) structural ceiling anchor 1.0 kN dynamic load at room centre; (b) DALI/RGB controllable lighting with floor-level switch + occupant control; (c) acoustic wall panels Class A (αw ≥0.9) to achieve RT60 ≤0.6 s; (d) blackout blind to all glazing. Cross-ref with E (electrical) and S (structural) — see existing findings on ceiling fixings. | GA Plan 11001: 6.76 m² SENSORY ROOM 0.10; 10.06 m² SENSORY ROOM 0.27. No equipment, lighting control, ceiling anchor or acoustic finish noted on plan or in any sub-drawing. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\11000_GA Plans\11606-XX-L00-DR-RHA-AR-11001- GA Plan - Ground Floor.pdf | EMPLOYER | OPEN
H-006 | HIGH | HEALTHCARE | GYM_PAEDIATRIC_PHYSIO_PROVISIONS | 11606-76-XXX-DR-RHA-AR-57006 Furniture Details — 0.07 Gym Room | Gym 0.07 — 31.59 m², 7289 × 4324 mm | HBN 11-01 Facilities for primary and community care premises §6 (therapy gym); CSP/Chartered Society of Physiotherapy guidance for paediatric physiotherapy facilities; HSE Estates standard for occupational therapy spaces. | 0.07 Gym layout shows only a TV, base units and a basin — no ceiling-mounted swing/track anchor, no padded wall protection, no mirror wall, no sprung floor (the floor finishes plan lists F3 = 3.2 mm sport linoleum but this is NOT a sprung-floor system — paediatric physiotherapy requires either a sprung sports floor or padded matting capability). No equipment storage adjacent (the nearest store 0.14 is across Hall 03). Ceiling height not noted on layout but section drawings should confirm ≥3.0 m clear for swing/track installation. As scheduled, this is a generic activity room labelled 'Gym', not a paediatric physiotherapy gym, and will not meet CSP equipment standards. | ARCH_DESIGNER to (i) confirm and label ceiling clear height ≥3.0 m on section drawings 30001/30002; (ii) add ceiling-mounted track anchor structural provision (cross-ref with S); (iii) revise FF&E to add padded wall panels (1500 mm high to one long wall), full-height mirror to one elevation, sprung-floor build-up specification; (iv) reallocate 0.14 STORE or part of it as direct-access gym equipment store; (v) clarify with CRC clinical lead PT the equipment schedule (plinth, parallel bars, ramps). | 0.07 GYM PLAN AR-57006: shows base units, basin, 65'' wall-mounted TV; no track, no padded walls, no mirror. Floor Finishes AR-13002: F3 = 3.2mm Marbled Linoleum Sheet (Forbo Sport). | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\50000_Details\11606-76-XXX-DR-RHA-AR-57006- Furniture Details - 0.07 Gym Room.pdf | ARCH_DESIGNER | OPEN
H-007 | HIGH | HEALTHCARE | INFECTION_PREVENTION_CONTROL | 11606-XX-ZZZ-SH-RHA-AR-40009 Internal Finishes Schedule + AR-13002 Floor Finishes | All clinical zones (Therapy 0.12 / 0.23–0.28, Group Therapy 0.08, Gym 0.07, Sensory 0.10/0.27) | HBN 00-09 Infection Control in the Built Environment §4 (Floor finishes), §5 (Wall finishes), §6 (Ceilings); HSE Code of Practice for Infection Prevention and Control in Healthcare; HIQA Standards Theme 6 (Health and Wellbeing) infection-prevention requirement. | Internal Finishes Schedule AR-40009 calls 'Moisture-resistant suspended plasterboard with washable emulsion paint, soft sheen' as the standard clinical ceiling. This is NOT a Class I hygienic ceiling for clinical/wet areas — HBN 00-09 requires impervious, easy-clean, smooth, jointless or sealed-joint ceilings in any clinical activity space, washable to BS EN 13501 cleaning regime. Floor finishes show F1 = 2.5 mm Forbo Marmoleum/linoleum across therapy rooms — linoleum is organic (linseed oil based) and not the welded sheet vinyl that HBN 00-09 specifies for clinical infection prevention; it is not welded as a continuous impervious membrane and joints are vulnerable. Cove detail to walls noted only in cabinetry detail (floor coved up to plinth face) not at general wall–floor junction. No specification of antimicrobial wall protection (impact rails at wheelchair height ~900 mm) in clinical zones. | ARCH_DESIGNER to (i) upgrade ceiling spec in clinical rooms to a Class I hygienic ceiling (e.g. Armstrong Bioguard, Knauf Cleaneo Hygienic) or smooth sealed plasterboard with antimicrobial paint and welded service penetration seals; (ii) change F1 to welded sheet vinyl (Polyflor 2000PUR or equal) with hot-welded seams and full coved skirting 100 mm up the wall in all clinical/therapy rooms; (iii) add impact protection rail (Acrovyn or equal) at 900 mm to all clinical corridors and therapy rooms; (iv) confirm joinery wash-up zones in therapy rooms are sealed silicone to wall finish. | AR-40009: 'Moisture resistant, Suspended plasterboard with washable emulsion paint, Soft Sheen finish, Colour - White' (all therapy/clinical rooms). AR-13002: F1 = 2.5mm Forbo Marbled Linoleum Sheet, LRV 45%, R9 (Forbo Fresco). | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\40000_Schedules\11606-XX-ZZZ-SH-RHA-AR-40009- Internal Finishes Schedule.pdf | ARCH_DESIGNER | OPEN
H-008 | HIGH | HEALTHCARE | CLEANERS_STORE_SLUICE | 11606-XX-L00-DR-RHA-AR-11001 GA Plan + AR-40006 Sanitary Schedule + AR-40009 Finishes | Cleaners Store 0.03 — 8.82 m² | HBN 00-10 Welfare Facilities §6 (Domestic services accommodation); HSE Code of Practice for IPC §6.4 (cleaning equipment storage); HTM 64 (sanitary assemblies — sluice/bucket sinks). | Sanitary Schedule lists 0.03 Cleaners Store with SIN013 (sink + basin Janitorial unit with hinged bucket grating) — correct. BUT no separate sluice for soiled water from incontinence/changing waste (a CDNT serving children with severe disabilities will generate sluice loads daily). No drying rail / mop rack scheduled. No chemical lock-up cupboard scheduled (HSE COSHH requires lockable storage in any building accessible by children/vulnerable adults). Floor finish F6 epoxy is correct. No ventilation extract noted on plan (cross-ref M). Cleaners store is the wet-services hub for IPC compliance and needs to be specified completely now. | ARCH_DESIGNER + M to (i) add wall-mounted sluice or confirm Janitorial unit serves dual function; (ii) add mop drying rail (RAI902 type), shadow board for colour-coded cleaning equipment (national HSE colour coding), and lockable chemical cabinet to FF&E; (iii) M-Engineer to confirm extract ventilation 10 ach to remove cleaning chemical vapour; (iv) add hand-wash basin separate to sluice (HBN 00-10). | AR-40006: 0.03 CLEANERS STORE — SIN013 Janitorial sink+basin combination, SNU012 SINK UNIT single bowl, TAP815 combination assembly. No CIS005 cistern, no drying rail RAI902, no chemical cabinet. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\40000_Schedules\11606-XX-ZZZ-SH-RHA-AR-40006- Sanitary Schedules.pdf | ARCH_DESIGNER | OPEN
H-009 | HIGH | HEALTHCARE | KITCHEN_OPERATIONAL_BRIEF | 11606-73-ZZZ-DR-RHA-AR-57012 Kitchen Layout — Room 0.17 | Kitchen 0.17 — 21.20 m² + Kitchenette 0.39 — 7.19 m² + Activity Room 0.20 kitchenette | FSAI Code of Practice for Food Service in Healthcare Settings; HSE Food Safety Authority Ireland guidance; OT Life-Skills training kitchen — Royal College of Occupational Therapists (RCOT) facility standard; FSC Condition 5 (only applicable if deep fat fryer present). | Kitchen 0.17 layout AR-57012 is a hybrid — it shows a kitchen island and counters with two undercounter refrigerators, microwave and oven, splashbacks 'Whiterock Satins', and a fire counter shutter (FS-1) — suggesting it is BOTH a service catering kitchen AND/OR an OT training kitchen. The brief is unclear. If it is a service kitchen for meals to ~30 service users (which a CDNT day centre with Dining Hall 0.16 at 39.79 m² implies), it requires FSAI-compliant separation: separate clean/dirty zones, dedicated hand-wash basin, separate prep sink and wash-up sink, dishwasher with thermal sanitisation, ventilation canopy with grease filtration. AR-57012 shows one combined sink with drainer — inadequate. There is no clear separation of food handling and therapeutic activity. If it is a therapy/OT kitchen the work surfaces are too high (850 mm) for child use and there is no height-adjustable section. | EMPLOYER to confirm Kitchen 0.17 function: (A) Service catering for ~30 users — then ARCH + M to apply FSAI Code: separate prep/wash-up sinks, dedicated hand-wash, grease canopy extract, food-grade vinyl floor (currently F1 linoleum — wrong), wall finish to Whiterock to ceiling. (B) OT life-skills training kitchen — then add lower (760 mm) section with knee-clearance, dual cooker control accessible/non-accessible heights, child-safe induction (not gas). The current hybrid layout serves neither well. | AR-57012 Kitchen Layout Room 0.17: 'Fire Counter shutter FS-1', '600 600 600 600 600' undercounter cabinets, 'Whiterock Satins' splashback, two Undercounter Refrigerators, 1900 mm island unit. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\50000_Details\11606-73-ZZZ-DR-RHA-AR-57012- Kitchen Layout - Room 0.17.pdf | EMPLOYER | OPEN
H-010 | HIGH | HEALTHCARE | BREAKOUT_LIGATURE_RISK | 11606-72-XXX-DR-RHA-AR-57004 Breakout Room Seat | Breakout Room 0.13 — 7.86 m² | HBN 03-01 Adult Acute Mental Health Units / RCPsych anti-ligature principles applied to disability services with self-injurious behaviour risk; HIQA Standards Theme 5 (Effective Services) Standard 5.2 — environment safe for individuals with behaviours that challenge. | Breakout Room (0.13, 7.86 m²) is designated as a meltdown/recovery space — typical CRC use is for ASD or behaviour-of-concern de-escalation. AR-57004 specifies fabric & foam upholstery with timber-veneer panelling. No ligature-risk assessment of fittings, no specification of soft-fall flooring beyond standard vinyl, no controllable lighting, no panic alarm, no observation window to corridor specified. Window blackout blind cord is a known ligature point — Blind Schedule AR-40005 should be checked for child-safe operation. Door D0.013 ironmongery Set [check] — must permit external override (staff entry under all conditions) but not be self-locking from inside. | ARCH_DESIGNER to confirm specification (a) door ironmongery set with anti-barricade hinge + staff override key; (b) cordless / motorised blackout blind (no pull cord) per BS 8300-2 §15.4; (c) all wall fixings flush (no protruding hooks/rails); (d) ceiling-mounted PIR-controlled DALI dimmable lighting with no exposed cord; (e) panic alarm to staff station (Reception/Manager 0.18) — cross-ref with E. | AR-57004: 'Fabric and foam upholstery', 'Euroclass B white oak veneer panelling', 'Fire Performance of Upholstery: Upholstery in seating should, when tested in accordance with I.S. 254:1983, pass the smouldering cigarette test and Ignition Source Grade No. 5 Test'. No anti-ligature, no panic alarm noted. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\50000_Details\11606-72-XXX-DR-RHA-AR-57004- Furniture Details - Breakout Room Seat.pdf | ARCH_DESIGNER | OPEN
M-001 | HIGH | M&E | DOCUMENT_HYGIENE | M&E Drawing Issue Sheets (1743_Drgissue 2C) | Drawing Circulation block, all 3 issue sheets | Appointment register coherence; SI 9/2014 (designer identification) | Fire Consultant identified as 'TBC' on all 3 M&E issue sheets. Fire Consultant has been appointed (ORS — Conor Jordan signed Stage 2C Part B report). Appointment register out of sync. Coordination instructions to M&E may not flow to fire consultant. | Update M&E issue sheets to identify Fire Consultant as 'ORS' and add to circulation. Reissue. | M&E Issue Sheet (all 3 sheets): 'Fire Consultant: TBC'. Fire Report cover: signed by Conor Jordan, ORS Fire Safety Lead. | 1743_Drgissue 2C-Issue Sheet 1/2/3 of 3.pdf + 22481-Stage 2C Report p.5 | ME_DESIGNER | OPEN
M-005 | HIGH | MECHANICAL | Heating / NZEB capacity | Mechanical Specification.pdf | Heat pump capacity inconsistent in spec — 22 kW unit labelled but 30 kW data table appended | PW-CF5 Schedule (Particular Requirements) Clause 3 — design intent must be unambiguous; CIBSE Guide B1 §2 (Heat source sizing); TGD L 2022 NZEB Part L (oversized heat pump degrades SCOP/SEER and Primary Energy) | Tenderers cannot price reliably (22 kW vs 30 kW = ~35% capacity divergence and different electrical infrastructure, plinth size, acoustic envelope, F-Gas pre-charge). Risk of post-award contract claim, BER/NZEB recalculation, and structural roof loading change. Risk of fuse/cable undersizing if 30 kW unit installed on 32 A/6 mm² circuit. | M&E Designer to confirm scheduled duty (kW), associated electrical load, refrigerant charge and corresponding model number; reissue Heating Schedule and Bill Items 56-01/02 pre-tender. Coordinate with Elec Designer on cable size, MCB rating, RCD type. | Section 9.01 / 9.02: 'LPHW Outdoor Monoblock Units 22kW – 2 No' and '2 no. 22kw heat pump outdoor unit'. Same section 9.02 Performance Data tabulates 'Heating Output at 35°C Flow: 30.10 kW … 45°C 30.00 kW … 55°C 30.00 kW' and 'Maximum Operating Current: 22.8 A … Supply Fuse Rating 32 A … Cable 5G x 6mm² H07RN-F'. Bill Item 56-01/56-02: '22 kw'. | Mechanical Specification.pdf §9.01 (LPHW Heatpump general description) ¦ Mechanical Specification.pdf §9.02 (Technical Requirements + Performance Data table) ¦ Mechanical Specification.pdf Bill of Quantities §56-01, 56-02 | ME_DESIGNER | OPEN
M-006 | HIGH | MECHANICAL | Fire safety interlocks (Condition 5) | 22481-Stage 2C Report-Part B Compliance.pdf | Kitchen — FSC Condition 5 (deep-fat-fryer suppression + Lock Stop) not addressed in Mechanical Spec | FSC Grant 19/08/2025 Condition 5; I.S. EN 16282-7:2017 Components for ventilation in commercial kitchens — Fire suppression systems; TGD-B 2024 §3.5; BS 6173 (gas/electric isolation); Health Act 1947 Section 31 | Either (a) confirm in writing no deep-fat fryer (closes Condition 5 — but Lock Stop is still required wording in many Fingal FSC condition sets and best practice for a healthcare kitchen with combustible cooking risk) or (b) full IS EN 16282-7 suppression package, cause-and-effect interlock to L1 detection, fail-safe gas/elec isolation. Currently un-priced — major tender risk. | ME Designer (with Architect + Fire Consultant + HSE Estates) to (1) issue written confirmation that no deep-fat fryer will ever be deployed in Kitchen 0.17 and obtain Fingal/Dublin Fire Brigade acceptance, or (2) add full suppression specification (system type, agent, nozzles, duct heat detection, fusible link spec, FA interlock cause-and-effect matrix line, Lock Stop on route of escape, gas/elec shut-off relay, six-monthly service regime, fire safety register entry). Mark Bill of Quantities accordingly. F-006 raised by Fire reviewer also applies. | Fire Report Condition 5: 'Where deep fat frying equipment is provided … the cooking equipment and associated ductwork shall be protected by a fire suppression system … installed in accordance with IS EN 16282-7 … interfaced with the electrical/fuel supply systems (to shut off on activation) and with the fire detection and alarm system … suitable heat detection is to be provided in the extract ductwork … A suitably located "Lock Stop" (electrical knock off) switch is to be provided for manually isolating any gas and electrical supply in the kitchen area (switch to be located on route of escape). Maintenance testing and inspection details are to be recorded on the fire safety register.' Mech Spec §13.0 Fire Fighting Installation lists only handheld extinguishers and 'Fire Blankets installed within kitchen areas' — no suppression, no Lock Stop, no kitchen-extract heat detection, no maintenance regime. Arch Room 0.17 Kitchen FF&E Schedule shows electric 4-burner cooker COO002, microwave OVE015, airfryer FRY900 (Group 3 loose), no deep-fat fryer. | 22481-Stage 2C Report-Part B Compliance.pdf p.3 Condition 5 ¦ Mechanical Specification.pdf §13.0 Fire Fighting Installation ¦ 11606-XX-L00-DR-RHA-AR-60017 Kitchen FF&E Schedule | ME_DESIGNER | OPEN
M-007 | HIGH | MECHANICAL | Coordination / FF&E vs Building Services | 11606-XX-ZZZ-SH-RHA-AR-40006 Sanitary Schedule Room 0.06 'HOI001'.pdf | Ceiling-mounted track hoist HOI001 in C/P WC 0.06 — no mechanical/structural coordination, no manufacturer schedule | BS EN ISO 10535:2021 (Hoists for transfer of disabled persons); HBN 00-02 Sanitary spaces (Changing Places); BS 8300-2:2018 Table 8 (Changing Places Toilet minimum provisions inc. ceiling track hoist); HSE National Estates standard for Changing Places Facility; PW-CF5 Clause 9 (interface management); CIBSE Guide M (maintenance access) | (a) Brand/manufacturer governs structural pull-out load (250 kg SWL typical, up to 500 kg bariatric) — C&S beam upstand and pad detail un-quantified; (b) electrical isolator and charging point not on Elec sanitary RDS; (c) ceiling void clash with MVHR duct, smoke damper, sprinkler (if any) un-checked; (d) project brief specifically flagged CARBITAN vs ARJO vs SEA — no design freeze evidenced. Cross-discipline RFI required. | ME Designer to (1) confirm governing hoist brand and model in writing with Client (HSE Estates) — the brief flagged the conflict; (2) issue an addendum mechanical/coordination note locking structural support type (H-track end pads + structural traveller spans), electrical 230V supply + isolator location, BMS interface (if any), ceiling void access strategy; (3) verify FF&E vs M&E scope split and update bill split. | Sanitary Schedule (AR-40006) Room 0.06 C/P WC: 'HOI001 — TRACK HOIST - ceiling mounted H style full coverage of space, Count 1'. Mechanical Specification has zero references to 'hoist', 'track', 'ARJO', 'CARBITAN', 'SEA', 'Liko' or ceiling-mounted patient lift. Mechanical Drawings 1743_50–59 (sampled) contain no hoist coordination notes. No Mechanical Schedule for hoist motor electrical isolation, battery charging point location, or service access in ceiling void. | 11606-XX-ZZZ-SH-RHA-AR-40006 Sanitary Schedule Room 0.06 'HOI001' ¦ Mechanical Specification.pdf (absence — full-text search returns 0 hits) ¦ Project Brief flagged conflict CARBITAN/ARJO/SEA | ME_DESIGNER | OPEN
M-008 | HIGH | MECHANICAL | F-Gas / Refrigerant compliance | Mechanical Specification.pdf | F-Gas Regulation 2024/573 obligations not addressed (logbook, leak check, certified installer, banned-substance check) | Regulation (EU) 2024/573 on fluorinated greenhouse gases (effective 11/03/2024, replacing EU 517/2014); Irish SI 281/2017 as amended; F-Gas Article 5 (leak check intervals based on CO2eq tonnage); Article 6 (record-keeping); Article 11/14 (placing-on-market restrictions for stationary equipment ≤12 kW vs >12 kW); Article 10 (certified personnel) | R32 GWP = 675. 2×5 kg = 10 kg × 675 = 6,750 kg CO2eq = 6.75 tonnes CO2eq — EACH unit (5 kg × 675 = 3.375 t CO2eq) is BELOW the 5-tonne CO2eq leak-check threshold but combined plant inventory is above. Spec must mandate: (a) F-Gas Certified Company installer; (b) commissioning F-Gas form lodged with EPA; (c) leak detection / annual leak check obligation in O&M; (d) end-of-life refrigerant recovery clause. New 2024/573 also introduces phased-down quotas — confirm R32 still permitted at install date (allowed through to 2027 cap; longer for split <3 kg). | ME Designer to insert F-Gas compliance section into Spec covering Certified Company requirement, leak detection (electronic or manual), F-Gas logbook in O&M Section 10 (Statutory Certificates), refrigerant declaration, end-of-life recovery clause. Confirm DHW heat pump refrigerant (likely R744/CO2) and add transcritical-cycle commissioning notes. | Mech Spec §9.02 lists 'Refrigerant Type: R32 (low GWP) — Charge: 5000g, factory pre-loaded and hermetically sealed' for the 22 kW heat pump (×2 units = 10 kg R32 total). DHW heat pump §9.03 is Mitsubishi QAHV-N560YA-HPB (-BS) (CO2 / R744 cycle — needs explicit confirmation). Spec has NO reference to F-Gas Regulation EU 2024/573, no leak detection on units, no logbook obligation, no F-Gas certified contractor requirement, no end-of-life recovery clause. | Mechanical Specification.pdf §9.02 Refrigerant System data ¦ Mechanical Specification.pdf §9.03 DHW Heatpump (Mitsubishi QAHV) ¦ Bill of Quantities §56-03 (Mitsubishi QAHV-N560YA-HPB(-BS)) | ME_DESIGNER | OPEN
M-009 | HIGH | MECHANICAL | Water Hygiene (TGD G / HTM 04-01 / L8) | Mechanical Specification.pdf | Water hygiene — Legionella Risk Assessment, BS 8558 / L8 compliance and tank water-quality regime not specified | TGD G 2022 (Hygiene — water systems); HTM 04-01 Safe water in healthcare premises (Parts A & B); BS 8558:2015 (Guide to the design, installation, testing and maintenance of services supplying water for domestic use within buildings); HSE 'Approved Code of Practice and guidance: L8' / ECDC Legionella guidance; HSE National Guidelines on the Control of Legionellosis in Ireland 2009/2021 | Healthcare day-care building with potentially immunocompromised users — no formal water safety plan exposes Client to HSA/HSE enforcement. Single-compartment tank fails HTM 04-01 'serviceability without loss of supply'. No microbiological commissioning means no baseline for ongoing monitoring. TMV3 specified only for showers and IPS taps — no service/cleaning schedule. | ME Designer to (1) add explicit reference to HTM 04-01 + BS 8558 + L8 + HSE Ireland Legionella guidance in §2.05 standards list; (2) require Legionella Risk Assessment by competent person (City & Guilds 6041-31 or similar) pre-handover; (3) specify pre-handover microbiological sample (TVC, E.coli, Legionella) on each sentinel outlet; (4) specify post-handover flushing regime to be inserted into O&M Section 11; (5) either change to twin-compartment tank or provide written justification for single-compartment with maintenance/turnover analysis; (6) add TMV-3 6-monthly service regime to O&M. | Mech Spec §10.0 Water Services is silent on (a) Legionella Risk Assessment requirement, (b) HTM 04-01 (not referenced anywhere in 117-page document), (c) BS 8558 (not referenced), (d) Approved Code L8 (not referenced). §10.03 Sterilization describes only chlorination at 50 mg/l for 3 hours but no post-handover flushing regime, no water quality test (TVC/coliforms), no sentinel outlet sampling. §10.07 specifies a single 4,500 L Format 30 break tank 'within exposed at roof level' — NOT a twin-compartment tank — turnover may exceed 24 h at low occupancy creating Legionella risk in a healthcare day-care building serving immunologically vulnerable users. No TMV-3 service regime, no expansion-vessel hygiene. | Mechanical Specification.pdf §10.0 Water Services ¦ Mechanical Specification.pdf §10.03 Sterilization ¦ Mechanical Specification.pdf §10.07 New Cold Water Storage Tank ¦ Mechanical Specification.pdf §10.18 Thermostatic Showers | ME_DESIGNER | OPEN
M-010 | HIGH | MECHANICAL | Water hygiene / backflow | Mechanical Specification.pdf | Backflow prevention / Category 5 risk at sluice and clinical outlets — no I.S. EN 1717 categorisation | I.S. EN 1717:2000 Protection against pollution of potable water in water installations; Irish Water Standard Details TGD-030 (mains water); BS 8558:2015 §4 (Fluid category classifications); HTM 04-01 Part A §6 (Category 5 protection for healthcare sluice/dirty utility) | Category 5 (microbiological / faecal contamination) risk from janitor's sluice and any dirty utility back-feeding boosted mains and contaminating CWS storage — public-health offence under European Communities (Drinking Water) Regulations 2014. Irish Water may refuse connection without certified backflow strategy. | Add I.S. EN 1717 reference and a Backflow Strategy section. Categorise every outlet (Category 2/3/4/5). Provide RPZ (BA) valve on boosted CWS at point of entry to clinical risk zones, Type AUK3 tap (air-gap) on janitor sink, Type AA/AB tank inlet (already partially achieved by Format 30 ball valve — confirm air-gap dimensioning). Add commissioning RPZ test certificate to handover documents (Section 10 Statutory). | Mech Spec §4.10b 'Mains water Piping' references TGD-030.1 (correct) but I.S. EN 1717 is NOT cited anywhere in the spec. Spec §4.15 mentions only 'N.R.V.'s shall also be fitted to all dishwasher and other machines requiring domestic water connections' — single check valve is Category 2 protection only. Sanitary Schedule Room 0.03 Cleaners Store contains SIN013 (sink + basin combination janitorial unit) — Category 5 fluid risk (microbiologically contaminated). No RPZ valve, no Type AB/AA air-gap, no AUK3 tap is specified. | Mechanical Specification.pdf §4.10b Mains Water Piping ¦ Mechanical Specification.pdf §4.15 Connection to fixtures ¦ AR-40006 Sanitary Schedule Room 0.03 SIN013 | ME_DESIGNER | OPEN
M-011 | HIGH | MECHANICAL | Spec hygiene / fire-damper standards | Mechanical Specification.pdf | Fire-damper standards stale — spec cites BS 5588 Part 9 (withdrawn) and BS 476 Part 8 (superseded for resistance to fire) | TGD-B 2024 (Fire Safety) §3.5.7 'Accommodation of services in compartment walls/floors'; I.S. EN 1366-2 (Fire resistance tests for service installations — fire dampers); I.S. EN 15650 (Ventilation for buildings — Fire dampers); BS EN 13501-3 (Classification of dampers); BS 5588 series withdrawn and replaced by BS 9999 / I.S. EN; BS 476 series partially superseded by I.S. EN 13501-2 | Spec basis-of-design is technically stale and inconsistent with the Fire Cert Condition 3 (TGD-B 2024). Tenderers may price old technology, miss CE-marked EN 15650 dampers, or supply dampers not classified to EN 13501-3 (EI 60 / EI 120 / S). Risk at Fire Officer hand-over inspection. | Update §5.02.13 / 5.03 / 5.07 to cite I.S. EN 1366-2, I.S. EN 15650, I.S. EN 13501-2/3, BS 9999:2017; require dampers to be CE-marked EI 60 (S) where penetrating compartment lines, EI 120 (S) at protected stair/shaft where required; require installed-position commissioning certificate per BSRIA BG 50. | Mech Spec §5.02.13 and §5.07: 'they are to be protected in full accordance with the relevant recommendations of BS5588 : Part 9, which it is noted will typically involve the fitting of fire dampers at ductwork penetrations' … 'Fire and smoke dampers shall be constructed to BS 476 Part 8: 1972' … 'tested to B.S. 476 Part 20 1987 for a period of two hours and a Test Certificate shall be provided'. §5.03 cites 'BS5588 Part 9(1989)' for fire-resistant ductwork (Method 3) and Firebar BW11. Fire Report Condition 3 expressly requires services in compartment walls 'in accordance with 3.5.7 of TGDB 2024' (the current standard). | Mechanical Specification.pdf §5.02.13 Smoke/fire dampers ¦ Mechanical Specification.pdf §5.03 Ductwork: Fire Resistant ¦ Mechanical Specification.pdf §5.07 Smoke/fire dampers ¦ 22481-Stage 2C Report-Part B Compliance.pdf Condition 3 | ME_DESIGNER | OPEN
M-012 | HIGH | MECHANICAL | Spec hygiene | Mechanical Specification.pdf | Withdrawn standards proliferation throughout spec (BS 5486, BS 1387, BS 5588, BS 4814, BS 4504, BS 142, IS 238:1980, BS 89, BS 775, VDE 0660, IS 290/291, IS 123, BS 2871, BS 2989, BS 6071) | PW-CF5 Schedule Particular Requirements (latest editions of standards apply); CIBSE Guide M (current standards); engineering best practice; HSE Estates technical standards (current editions) | Tender ambiguity, risk of contractor compliance challenge, non-compliance with PW-CF5 'latest standards' obligation, gap between spec and BCAR sign-off. CIBSE peer would refuse to validate the document. | Designer to perform a full sweep replacing every named standard with the current edition. Priority replacements: BS 5588-9 → I.S. EN 1366/15650; BS 476-8/20 → I.S. EN 13501-2/3 / EN 1366-2; BS 5486 → I.S. EN 61439; BS 1387 → BS EN 10255 (consistently); BS 4814 → BS EN 13831; BS 4504 → BS EN 1092; BS 142 → BS EN 10226; IS 238:1980 + BS 6071 → BS EN 1057; IS 290/291 → 2015 editions; BS 88 → BS EN 60269; BS 775 → EN 60947-4-1. | Numerous obsolete/withdrawn references inc.: §2.05 'EMC Directive 89/336/EEC' (superseded by 2014/30/EU); §4.02 'BS 1387' (withdrawn — replaced by BS EN 10255 which is also cited inconsistently); §4.06 'BS 142' for threaded pipe (withdrawn — use BS EN 10226); §4.21 'B.S. 4504 Part 1: 1969' (withdrawn — use BS EN 1092); §4.27 cites superseded BS series; §5.02.13 'BS 476 Part 8: 1972' / 'BS 476 Part 20 1987' (superseded by EN 13501-2); §9.18 'B.S. 4814:1990' for expansion vessels (withdrawn — use EN 13831); §12.04 'BS 5486 Part I - Form 3' (withdrawn — use BS EN 61439); §12.17 'VDE 0660 for NH type CEE 16 for DZ type and BS 88' (BS 88 superseded by EN 60269); §12.18 'BS 775' for contactors (withdrawn — use EN 60947-4-1); §13.02 'I.S. 291: 1986' (superseded by I.S. 291:2015 + I.S. 290:2015 — references also cited as 'I.S.290' without year); §4.04 'BS 2989: 1982 Class B' (superseded by EN 10346); §10.06 'IS 238 : 1980, BS 6071 Cu-DHP' (BS 6071 withdrawn — use BS EN 1057 for plumbing copper); §14.07 'I.S. EN ISO 9002: 1994 / BS EN 1329-1:2000' (ISO 9002:1994 was withdrawn in 2000); §8.02.2 'IS 123' for water mains (superseded). | Mechanical Specification.pdf §2.05 / §4.02 / §4.06 / §4.21 / §4.27 / §5.02.13 / §9.18 / §10.06 / §12.04 / §12.17 / §12.18 / §13.02 / §14.07 | ME_DESIGNER | OPEN
M-100 | HIGH | MECHANICAL | DRAWING_STATUS | Drg 1743_57_01 Ventilation Roof Layout | Title block / drawing status | PW-CF5 Employer-Designed contract — all tender drawings must be issued at Tender status; CIBSE Guide G; Code of Practice for Construction Information | Drawing 1743_57_01 (Ventilation – Roof Layout) carries a large DRAFT watermark across the sheet while being issued in the Tender pack. Tenderers will exclude or qualify pricing for roof-mounted MVHR ducts, attenuators, intake/exhaust hoods, condensate routes and structural roof penetrations — creating provisional sum exposure of the order of €30k-€80k at post-tender stage. | Re-issue 1743_57_01 with DRAFT watermark removed and revision cloud / rev table populated with issue date and 'TENDER' status; re-distribute via eTenders addendum at least 7 working days before 17:00 Wed 10-Jun-2026. | Drawing 1743_57_01 sheet shows 'DRAFT' watermark across the centre of the sheet; title block shows status 'TENDER' but content not finalised. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_57_01.pdf | ME_DESIGNER | OPEN
M-101 | HIGH | MECHANICAL | DRAWING_STATUS | Drgs 1743_59_00 and 1743_59_01 (Water Services & Heating/BMS schematics) | Title block — drawing status | PW-CF5 tender information requirements; BSRIA BG 6 (Design Framework for Building Services) | Both critical schematic drawings (proposed water services schematic 59_00, proposed heating + BMS schematic 59_01) show drawing status field as 'N.T.S.O A1' rather than 'TENDER', with no rev/date/check entries. Schematics are the principal control & balancing reference for water and LPHW — tenderers cannot price the BMS panel, MCC outgoing ways, pulse meters or wiring without confirmed schematic status. | Re-issue 59_00 and 59_01 with status 'TENDER', revision cloud, issue date, drawn / checked initials; confirm BMS I/O schedule and MCC outgoing ways are FINAL not concept. | Drg 1743_59_00 and 1743_59_01 title block status field reads 'N.T.S.OA1' (not 'TENDER'); rev/date/drawn-by/checked-by fields are blank. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_59_00.pdf | ME_DESIGNER | OPEN
M-103 | HIGH | MECHANICAL | PLUMBING_DRAINAGE | Mech Spec §52 BoQ + Drg 1743_52_00 | Above-ground drainage / grease management | IS EN 1825-1/-2 (grease separators), IS EN 12056-2 (drainage above ground), Building Regs TGD-H, Fingal Co.Co. trade-effluent discharge requirements | No grease separator (interceptor) is provided on the kitchen sink/dishwasher discharges. BoQ §52 contains line items 52-01 to 52-10 but no entry for grease trap. The drainage layout 52_00 shows kitchen sink and dishwasher discharging direct to 50mm waste then to builder's upstand without any IS EN 1825 grease separator. Fingal Trade Effluent bye-laws and Irish Water Code of Practice require Class I or II separator on commercial food premises. Risk of drainage blockage, foul odours back into therapy/dining areas, and refusal of Irish Water connection. | Issue addendum: (a) confirm kitchen classification per IS EN 1825 (NS sizing); (b) add grease separator (typ. NS-2 to NS-4) to mech BoQ as new item 52-11 with sampling chamber and access for maintenance; (c) update Drg 52_00 to show separator location, maintenance access, and Irish Water connection sequence. | Mech BoQ §52 lists 52-01 to 52-10 with no grease separator. Drg 52_00 'SCHEDULE OF SOIL & WASTE SIZES' shows Dishwasher 40mm and Sink 40mm discharging to 50mm float without intercept. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_52_00.pdf | ME_DESIGNER | OPEN
M-105 | HIGH | MECHANICAL | VENTILATION_PRESSURE | Drg 1743_57_00 | Pressure relationships between rooms | HBN 00-04 §3.4 (pressure cascade in healthcare); CIBSE Guide B2 §2.4 (containment / contamination control); IS EN 16798-1 | Drawings 57_00/57_01 do not annotate any pressure relationships (e.g. WCs negative, kitchen negative to dining, dirty utility negative, clean store positive, plant room neutral). For a healthcare day-care with CRC clients who are immunologically vulnerable (children/adults with disability) this is a clinical-risk omission. Without specified pressure cascade, the MVHR units (MVHR-1 to MVHR-6) cannot be commissioned correctly. Risk of cross-contamination, odour migration kitchen→dining→therapy. | Issue ventilation pressurisation schedule as supplementary drawing: tabulate each room with target Pa (e.g. WCs -5 to -10 Pa, kitchen -10 to -15 Pa relative to dining, clean store +5 Pa, plant room -5 Pa). Add commissioning requirement for room pressure verification per BSRIA BG 49. | Drg 57_00 shows supply/extract values per room but no pressure cascade table; spec §11.03 mentions BMS compatibility but no pressure regime requirement. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_57_00.pdf | ME_DESIGNER | OPEN
M-107 | HIGH | MECHANICAL | PLUMBING_TMV | Drg 1743_53_00 + Mech Spec §53-06 | TMV3 distribution | HTM 04-01 Part A §4.21 (TMV3 selection), NHS D08 Specification, BuildCert TMV3 scheme, BS 7942 | Drg 53_00 shows 'TYPICAL SINGLE WASH HAND BASIN VALVE ARRANGEMENT' and 'TYPICAL DOUBLE WHB ARRANGEMENT' with thermostatic mixing valve. BoQ 53-06 calls for 'WRAS approved TMV3'. However: (i) no schedule of TMV outlets / set-points (41°C basin, 41°C shower, 38°C bath per HTM 04-01); (ii) no isolation valves shown per TMV (TMV must have strainer + isolation on hot, cold sides per HTM); (iii) no annual TMV servicing access provision noted for ceiling-mounted units in C-P WC; (iv) C-P WC adult-change shower (Changing Places) needs TMV3-compliant outlet — not explicitly scheduled. | Issue (a) TMV schedule with location, outlet temp, model, BuildCert TMV3 cert no.; (b) update typical detail to show isolation+strainer+test plug per HTM 04-01 Fig 7; (c) confirm C-P WC shower & basin TMVs are TMV3 with weekly thermal-balance verification; (d) add annual servicing access requirement in O&M. | Drg 53_00 'TYPICAL SINGLE WASH HAND BASIN VALVE ARRANGEMENT' shows TMV but no isolation/strainer detail; BoQ 53-06 'Complete supply, installation and commissioning of WRAS approved TMV 3 shower and wash hand basin thermostatic valves'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_53_00.pdf | ME_DESIGNER | OPEN
M-108 | HIGH | MECHANICAL | PLUMBING_STORAGE | Drg 1743_53_00 | Cold water storage tank — sizing and access | HTM 04-01 Part A (CWS storage), BS 8558, BS EN 806-2, HSE L8 (Legionella), HBN 00-09 | Drg 53_00 specifies 'FORMAT 30 CWS TANK 1,275mm × 1,200mm × 850mm' (≈1,300 L). For a day-care with ~80 users + staff plus DHW pre-heat, 24h storage at 45 L/person/day = 3,600 L. Tank is marginal/undersized. Also (i) no break-tank category-5 protection at incoming main shown, (ii) no warning/overflow pipe routing detailed, (iii) tank turnover time not stated — HTM 04-01 requires ≤24h turnover to avoid stagnation, (iv) no insulated lid + insect screen specified explicitly on drawing. | Issue addendum: (a) calculate CWS demand per HTM 04-01 Part A, confirm tank sizing; (b) confirm category 5 AB air-gap break-tank required at incoming main per IS EN 1717; (c) detail overflow + warning pipe + tundish + lid + screen; (d) add tank turnover stated on drawing. | Drg 53_00: 'FORMAT 30 CWS TANK 1275 (l) x 1200 (w) x 850 (h)mm — L1280 W1185 H780'. No demand calc, no tank category, no turnover statement. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_53_00.pdf | ME_DESIGNER | OPEN
M-110 | HIGH | MECHANICAL | HEATING_DISTRIBUTION | Drgs 1743_56_00 + 1743_56_01 (heating loops) | Underfloor heating selection for therapy/sensory variable occupancy | CIBSE Guide A §1.6 (thermal comfort); CIBSE TM52 (overheating); HBN 26 (heat-up response); TGD L 2022 §2.3 | All heating is via under-floor loops fed from 6 manifolds (Drg 56_01) with no perimeter trim heat / no fast-response emitters. Underfloor systems have ~4-6 hour response lag, unsuitable for therapy and sensory rooms with high variability (group changes hourly, sensory rooms need rapid setpoint changes for behavioural / sensory regulation). Risk: rooms either too hot or too cold during sessions, with no operator-friendly local control. CRC client behavioural regulation depends on thermal stability. | Reconsider hybrid approach: UFH base load + low-temperature trim emitters (LST radiators or fan-coil tops) in sensory / therapy / activity rooms with PIR-linked occupancy override on BMS. If UFH-only retained, document acceptance of slow response in design risk register and confirm with HSE clinical/CRC end-user team. Provide thermal modelling demonstrating no overheating per TM52. | Drg 56_01 shows 6 manifolds zoning whole building with under-floor heating; Mech Spec §9.14 'underfloor heating system... loops are to provide heat evenly across the entire floor space of each zone'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_56_01.pdf | ME_DESIGNER | OPEN
M-112 | HIGH | MECHANICAL | PLANT_ROOM | Drg 1743_56_00 + 1743_55_00 plant room | Plant room ventilation, fire compartmentation, drainage | TGD-B 2024 §1.4 (compartmentation of plant rooms); CIBSE Guide B §4 (plant room ventilation); IS 3217 (emergency lighting in plant rooms); BS 5588 | Plant room (Room 0.31 / shown on 55_00 plant room layout) houses MCC, MDB, buffer vessel, cylinder, pressurisation unit, booster pumps and BMS panel — but no plant room ventilation rate is stated (CIBSE Guide B suggests 5-10 ACH min, more with electrical inverter heat gain), no fire compartmentation note (TGD-B Table 1.4 requires 60-min compartment), no plant room floor drain shown on Drg 52_00 (potential 400L buffer or 200L cylinder leak with no contained drainage path), and no plant-removal route study (replacement of 200L cylinder/400L buffer through corridor turns). | Add plant room ventilation calculation + spec'd grille on Drg 57_00; confirm 60-min FR compartmentation on architectural drawings; add floor gully on Drg 52_00 for plant room; produce plant-removal route study verifying largest item can be replaced through corridor / door swings. | Drg 55_00 'PLANT ROOM LAYOUT' shows pressurisation unit, buffer, cylinder, P1/P2/P3 pumps, MCC, MDB but no ventilation grille schedule, no floor gully, no compartmentation note. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_55_00.pdf | ME_DESIGNER | OPEN
M-113 | HIGH | MECHANICAL | FIRE_DAMPERS | Drgs 1743_57_00 + 1743_55_00 BMS | Fire dampers and cause-and-effect | TGD-B 2024 §B3 (compartmentation), BS 9999 §32, BS EN 15650 (fire dampers), BSRIA BG 27 (BMS interfaces with fire systems) | Drg 57_00 shows 'MOTORISED FIRE DAMPER' symbols at compartment-wall ductwork penetrations and Drg 55_00 shows 'MOTORISED FIRE DAMPER PANEL' linked to BMS, but: (i) no fire damper schedule (location / size / FR rating / fusible link or motorised, manufacturer); (ii) no cause-and-effect matrix between fire alarm panel (F-001 scope) and motorised fire damper panel; (iii) no annual drop-test access provision per BS EN 15650 §6.4; (iv) no interface with kitchen suppression (X-004) shown — kitchen extract fire damper must close on kitchen fire alarm not just whole-building alarm. | Issue fire damper schedule as supplementary drawing 57_02. Add cause-and-effect matrix (joint mech + fire). Add annual drop-test access requirement to O&M. Confirm kitchen extract isolation interfaced with kitchen-zone alarm and wet-chemical suppression release. | Drg 57_00 shows fire damper symbols on duct crossings but no schedule; Drg 55_00 shows 'MOTORISED FIRE DAMPER PANEL' with no I/O schedule. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_57_00.pdf | ME_DESIGNER | OPEN
M-121 | HIGH | MECHANICAL | FIRE_SUPPRESSION | Mech Spec §13 (fire extinguishers) + Kitchen scope | Sprinkler / wet-chemical kitchen suppression scope | BS 9251 (residential/domestic sprinkler systems), BS EN 12845 (commercial sprinklers), BS 6173 / IS EN 16282-7 (kitchen wet-chemical suppression), FSC condition 2025 | Mech Spec §13 lists portable fire extinguishers and 'Fire Blankets installed within kitchen areas' but: (i) no sprinkler system scope (yet drawings show MVHR/duct cross-refs to 'sprinkler sub-contractor' in §3.31 — internal contradiction); (ii) no wet-chemical kitchen suppression (Ansul-type) despite cooking proposed; (iii) no interface with Fire Alarm scope F-001. FSC granted 19/08/2025 — need to verify if a sprinkler condition exists. Tenderers will exclude sprinklers / wet-chemical at risk, with PC2/PC3 cost exposure. | Issue addendum confirming: (a) is BS 9251 / BS EN 12845 sprinkler system required by FSC? — if yes, separate BoQ section needed and clarified scope between Mech contractor and dedicated sprinkler sub; (b) wet-chemical kitchen suppression scope confirmed and priced; (c) interface matrix with Fire Alarm (F-001) and Kitchen Extract isolation. | Mech Spec §3.31 references 'sprinkler sub-contractor has failed to provide the necessary information'; §13 lists only portable extinguishers + fire blankets; no sprinkler or wet-chemical suppression scope. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Specifications\Mechanical Specification.pdf | ME_DESIGNER | OPEN
M-123 | HIGH | MECHANICAL | DHW_BUFFER_INSULATION | Drg 1743_53_00 + Mech Spec §10 | DHW dead-leg lengths and secondary return | HSE L8 ACoP §2.55, HTM 04-01 Part A §6 (dead-legs ≤2x pipe diameter or ≤1 m), BS 8558 | Drg 53_00 distribution shows long run from plant room (where cylinder is) across the building to remote outlets in therapy rooms, sensory rooms, accessible WCs and C-P WC — at the far end of the building from plant room (estimate >25 m). Drawing shows a secondary HWS return loop, but: (i) no maximum dead-leg length stated; (ii) outlets to TMVs at C-P WC and accessible WCs need to be within 2x pipe diameter of recirculating loop or ≤1 m to comply with L8/HTM 04-01; (iii) no temperature monitoring at end of secondary return shown; (iv) hot-water pre-heat coil position relative to heat-pump output not optimised (Drg shows pump P3 hot water secondary return — flow not stated). | Annotate Drg 53_00 with secondary-return reaches within 1 m of every outlet TMV. Add thermometer pocket at return entering cylinder (must read ≥55°C). Add temperature alarm on BMS for return ≤55°C. Confirm dead-leg <1 m to TMV per HTM 04-01. | Drg 53_00 distribution shows HWS, HWR loop and TMVs but no dead-leg stated and no return temperature monitor. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_53_00.pdf | ME_DESIGNER | OPEN
S-001 | HIGH | C&S | DOCUMENT_HYGIENE | C&S Drawing Register (DR01) | All 24 rows — Revision columns | BS 1192 / BS EN ISO 19650-2 §5.3 (revision control); SI 9/2014 Reg 9 (designer responsibility for issued info) | All Current Revision, Current Revision Date and Current Revision Description fields are blank. No revision control evidenced. Cannot demonstrate what version of any C&S drawing is the controlled current version. BCAR Assigned Certifier cannot accept drawings without revision control. | Populate revision data for every C&S drawing. Issue rev 0 'For Tender' if no prior revisions. Reissue register. | DR01: 26 drawing rows, all with empty Current Revision / Current Revision Date / Current Revision Description columns. | DR01 - DRAWINGS REGISTER.pdf | CS_DESIGNER | OPEN
S-002 | HIGH | C&S | DOCUMENT_HYGIENE | C&S Drawing Register (DR01) | Register header / column structure | CWMF ARM4 (tender pack standards); BS EN ISO 19650-2 | C&S register has no Status Code column and no Purpose-of-Issue column (unlike Architectural register which states 'P08-S' and Tender on every row). Tenderer cannot determine whether C&S drawings are issued For Tender, For Construction, or Preliminary. Material risk to pricing certainty. | Reissue C&S register with Status Code and Purpose-of-Issue columns populated (Tender) for every drawing. | DR01 columns: Sheet Number, Sheet Name, Sheet Issue Date, Designed By, Approved By, Current Revision, Current Revision Date, Current Revision Description — no Status Code or Purpose-of-Issue column. | DR01 - DRAWINGS REGISTER.pdf | CS_DESIGNER | OPEN
S-003 | HIGH | C&S | COMPLIANCE | C&S pack | Pack scope — structural calculation package | Eurocodes + Irish NAs; SI 9/2014 Reg 9 (Assigned Certifier requirements); BCAR Code of Practice for Inspecting and Certifying Buildings and Works | C&S pack contains drawings + 3 schedule spreadsheets (Bending Schedule, Surface Water Attenuation Cl 2309, Foundation Mesh Calculator) but NO structural design report, NO calculation package, NO design statement, NO Eurocode design basis. Assigned Certifier cannot sign Ancillary Cert for structural design without underlying calcs. Tenderer cannot validate buildability. | Issue structural design report including Eurocode basis (EN 1990/1991/1992/1993/1996/1997/1998 + Irish NAs as applicable), design loadings, calculation summary, and foundation justification. Confirm Geotechnical/Ground Investigation Report and reference SI in design. | Pack inventory: PDF DRAWINGS folder (drawings only), SCHEDULES folder (3 xlsx files for bending/attenuation/mesh), SPECIFICATION folder (1 spec PDF). No calc package, no design statement, no GI report referenced. | Pack manifest + DR01 register | CS_DESIGNER | OPEN
S-009 | HIGH | C&S | COMPLIANCE | All structural drawings | Standard NOTES box, note 3 | I.S. EN 1993-1-1 + Irish NA (Steel Design); I.S. EN 10025-2 (Hot-rolled structural steel — material grade designation); I.S. EN 1090-2 (Execution of Steel Structures — execution class must be unambiguous); BCAR SI 9/2014 Code of Practice (drawings must be unambiguous for tender). | Note 3 on every structural sheet ends 'It shall be protected as per the Specification Section H.O - System II . All steel to be grade .' (blank). The spec defaults to S275JR but the drawing leaves the grade open. Without a stated grade and execution class on the drawing, fabricators will price the lowest-cost grade (typically S235) and EXC1, exposing the project to a re-pricing variation when EXC2 / S275 is later enforced. Note also says 'execution class .' (blank — though spec implies EXC2). Inconsistent with spec clauses Ha.001/1 and Ha.002/1. | Re-issue all C&S drawings with note 3 fully completed: 'execution class 2 (EXC2) ... All steel to be grade S275JR (or S275JO where flange thickness exceeds 16 mm and exposed externally) in accordance with I.S. EN 10025-2.' Cross-check Spec H.O System II protection system matches paint scheme on schedules. | '3. Structural steelwork detailed on this drawing shall be execution class . It shall be protected as per the Specification Section H.O - System II . All steel to be grade ' | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\11001 - FOUNDATION PLAN.pdf | CS_DESIGNER | OPEN
S-010 | HIGH | C&S | COMPLIANCE | Specifications - Rathbeale Rd.pdf (122 pp.) | Section A.1.6, Section E.1, Section F (table at clause F.102 area), Section H (Ha.001/1) | I.S. EN 1990 + Irish NA (Basis of Structural Design); I.S. EN 1991-1-1 to 1-7 + Irish NAs (Actions — permanent, imposed, snow, wind, thermal, accidental); BCAR SI 9/2014 Code of Practice (Eurocode framework must be cited). | Specification cites EN 1992 (concrete), EN 1993 (steel), EN 1996 (masonry), EN 1997 (geotechnical) but never explicitly cites EN 1990 (basis) or EN 1991 (actions). National Annexes are only referenced for EN 206 (concrete) and partially EN 13670; no NA reference attached to EN 1992/1993/1996/1997 citations. Without basis-of-design and actions standards being formally adopted, derived design quantities (load combinations, partial factors, climatic loads) are floating — this is a fundamental BCAR design-statement gap. | Add a new Section A clause (or update A.4.0) listing the full Eurocode suite to be applied: EN 1990 + IS EN 1990:2002/A1:2005 NA; EN 1991-1-1 through EN 1991-1-7 each with IS NA; EN 1992-1-1 + IS NA; EN 1993-1-1 + IS NA; EN 1996-1-1 + IS NA; EN 1997-1 + IS NA. State design working life (50/100 yrs), Consequence Class (likely CC2 for the day-care building) and corresponding Reliability Class. | 'E.1.1 Comply with the requirements and recommendations of I.S. EN 1992 -1-1, Eurocode 2: Design of concrete structures - Part 1-1: General rules and rules for buildings, of I.S. EN 13670, ...' (no equivalent clause for EN 1990 or EN 1991 in the spec). | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SPECIFICATION\Specifications - Rathbeale Rd.pdf | CS_DESIGNER | OPEN
S-011 | HIGH | C&S | COMPLIANCE | Specification Section E.4 / Table E.4 + all structural drawings | Table E.4 row 6; drawings 11001, 50002, 50004, 50005, RC0001-0007 | I.S. EN 206:2013+A2:2021 + NA:2015+AC1:2017 (Concrete — specification, performance, production); I.S. EN 1992-1-1 Annex E (exposure classes XC/XD/XS/XF/XA); BCAR Inspection Notification Framework. | Table E.4 row 6 reads 'Exposure Class(es): as specified on the drawing(s)' but NO drawing carries an exposure class. Healthcare facility implies aggressive disinfectant cleaning regimes internally (XC3/XC4 internally for areas with humidity cycles, possibly XD/XC4 to externally exposed slabs, XA on retaining wall faces). Without exposure class, the concrete supplier cannot generate a compliant 'ND.2 Form A' (called up by spec clause E.4.3), cover-to-rebar is unverifiable, and the BCAR Ancillary Cert for concrete works cannot be signed off. | Add a 'Concrete Schedule' table to drawing 11001 (or a new generalcover/exposure sheet 50000) listing each element (strip foundation, GF slab, RC retaining wall, RC walls, RC roof slab, boundary wall rising wall, manhole bases) with: Strength class (e.g. C32/40), exposure classes (XC, XD, XF, XA where applicable), minimum cement content, max w/c ratio, max chloride class (Cl 0.20 for reinforced), nominal cover and Δc-dev. Cross-check against EN 1992-1-1 Table 4.1/4.2. | Table E.4 row 6: 'Exposure Class(es): as specified on the drawing(s)' — and the drawings do not specify any. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SPECIFICATION\Specifications - Rathbeale Rd.pdf | CS_DESIGNER | OPEN
S-012 | HIGH | C&S | STRUCTURAL_SAFETY | 50002 - Rear Retaining Wall.pdf | Sections B, C, D; Rear Retaining Wall Elevation | I.S. EN 1997-1 + Irish NA (Geotechnical Design — retaining structures); I.S. EN 1996-1-1 (where masonry is used as a retaining element); CIRIA C580 (Embedded retaining walls); TGD A. | The 'Rear Retaining Wall' is shown as 337 mm concrete blockwork (13 N/mm²) on a 900x300 strip foundation with no toe/heel projection, no rebar in the stem and no key. As drawn it is a brick-faced masonry wall founded centrally on a strip — geometrically incapable of resisting overturning if any retained height exists. Sections B, C, D show the wall stepping with the slope but give no retained-height dimension, no surcharge, no soil parameters, no drainage layer behind. Either (i) the wall does not actually retain (in which case label is misleading and contractor will price it wrong) or (ii) it is structurally unsafe as detailed. Risk: collapse onto adjoining property no. 55 / 55a (residential rear gardens visible on site plan). | RFI to clarify: (1) maximum retained height at sections B, C, D and at any point along the elevation; (2) if retaining: redesign as cantilever RC L-wall or gravity wall sized per EN 1997 with full toe/heel, vertical/horizontal reinforcement schedule, drainage detail and surcharge assumption (5 kN/m² minimum); (3) confirm boundary ownership and Party Boundary Wall agreement with adjoining owners; (4) confirm wall is non-combustible (already raised in Fire) and complies with Fingal planning condition heights. | '337mm Concrete blocks 13 N/mm2' on '900x300 RC foundation with 1 layer A393 mesh 50 cover' — no retained height dimensioned, no reinforcement in stem, foundation is centrally placed (zero toe/heel). | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50002 - Rear Retaining Wall.pdf | CS_DESIGNER | OPEN
S-013 | HIGH | C&S | STRUCTURAL_SAFETY | 50001 - 1-8 m Boundary wall details.pdf | Boundary Wall Elevation (1.8m), Section A, Site Plan | I.S. EN 1996-1-1 + Irish NA (Masonry — unreinforced wall stability against wind); I.S. EN 1991-1-4 + NA (Wind actions for free-standing walls); TGD A1.1. | The 1.8 m boundary wall is shown as a single-leaf 215 mm brick wall on a 337 mm blockwork rising wall, with movement joints at 4.5 m c/c but NO intermediate piers, NO buttresses, NO bed-joint reinforcement specified to top of wall (only generic 'provide bed joint reinforcement' on the typ. section), and NO wind calculation. For Swords (terrain category II, basic wind 24 m/s) a 1.8 m free-standing single-leaf 215 brick wall typically requires either piers at ~3 m centres or a thicker section. As detailed, risk of overturning in design wind event onto public footpath / patient drop-off area. Liability under H&SWWA 2005. | RFI to provide wind-load calculation per EN 1991-1-4 (Cs.Cd, force coefficients for free-standing walls Annex A clause A.4) showing the wall section is adequate, or add piers/buttresses at calculated centres. State bed-joint reinforcement product (e.g. Bekaert Murfor RND.4/Z) and vertical spacing. | '215mm width 1800mm hight Brickwall — EXPANSION JOINT @ 4.5m C/C' (no piers, no wind calc, no top restraint). | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50001 - 1-8 m Boundary wall details.pdf | CS_DESIGNER | OPEN
S-014 | HIGH | C&S | COORDINATION | 11003 - ROOF PLAN.pdf; 50004 - RC Roof Slab; Spec Section E | Roof Plan, Section L of 50004, no green-roof/PV loading clause in spec | I.S. EN 1991-1-1 + NA (Imposed roof loads, Category H/I); GRO Code for Green Roofs (Irl/UK); Fire Report Condition 6 (PV array) and Condition 7 (Green roof) — both fed from the Stage 2C Fire Cert package; SI 9/2014 (designs must coordinate across disciplines). | Roof Plan shows 365 m² of green roof but the structural specification contains ZERO references to green-roof saturated dead load (typical 100-180 kg/m² for extensive sedum saturated), maintenance/access live load (Category I, 1.5 kN/m² + 1.5 kN concentrated), wind uplift on PV array (Fire Condition 6 ref) or PV ballast / fixing pull-out. RC Roof Slab 50004 specifies only H16@200T and A393B mesh — pattern alone does not demonstrate adequacy for the worst superimposed load case. Risk: green-roof failure under saturation event; PV roof penetration leakage and structural overload. | (a) Add roof-load schedule to drawing 11003 / 50004: Dead = self-weight + finishes + saturated green-roof substrate (state in kN/m²) + PV array dead (state kN/m² over footprint + concentrated); Imposed Cat H = 0.6 kN/m² (Ireland NA) for non-accessible, OR Cat I plus 1.5 kN concentrated for accessible/maintenance; Snow per EN 1991-1-3 sk for Swords; Wind uplift per EN 1991-1-4 on PV. (b) Confirm structural designer has coordinated with the M&E PV consultant and the green-roof specialist supplier — name them on the Ancillary Cert allocation. | Roof Plan legend: 'Green Roof 365m²' — no loading note. Spec full text search returns ZERO hits for 'green roof', 'PV', 'photovoltaic', 'sedum' or 'saturated substrate'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\11003 - ROOF PLAN.pdf | CS_DESIGNER | OPEN
S-015 | HIGH | C&S | COMPLIANCE | Cl 2309 - SurfaceWaterAttenuation.xlsx; 12001 PROPOSED DRAINAGE; 12004 Surface Water Extension | Whole calc sheet; Sheet1 row labelled 'Engineering Hydrology by E.M. Wilson' | Greater Dublin Strategic Drainage Study (GDSDS) Regional Drainage Policy Volume 2 + the Greater Dublin Regional Code of Practice for Drainage Works (GDRCoP); Fingal County Council Development Plan 2023-2029 SuDS requirements; CIRIA C753 (The SuDS Manual); spec clause SD.10.x cites GDRCoP. | Surface water attenuation calc is dated 27.08.2024 (21 months stale), uses an 'Engineering Hydrology' / 'BRE Digest 365' / 'Wallingford Procedure / Flood Studies Report' methodology, and does NOT cite GDSDS, GDRCoP, FSU (Flood Studies Update) rainfall depths, or the Fingal-specific design storm. Climate-change uplift used is 30% (reasonable) but urban-creep allowance is bundled in. Permitted discharge stated as 2 l/s (matches the hydrobrake on 12001) but the calc itself derives a 100-yr permitted of 3.53 l/s and a Qbar of 1.36 l/s — the 2 l/s setting is ASSUMED, not derived from a Fingal pre-development consultation. Storage 96.0 m³ required vs 104.6 m³ provided in 0.7 m deep coarse-aggregate sub-base under permeable concrete — margin only 8.6%, very tight. Fingal may not accept and may require a separate Section 30/Section 16 discharge agreement. | Re-run the attenuation calc to GDSDS/GDRCoP & FSU rainfall (Met Eireann depth-duration-frequency curves for Swords gridpoint), confirm pre-development discharge consultation outcome with Fingal Drainage Section in writing (attach the email/letter), check climate-change uplift complies with current OPW guidance (currently 20% minimum, 30% for critical infrastructure), and confirm 30% void ratio assumption for sub-base aggregate is supported by geotextile/sub-grade design and product data. State exceedance flow path for storms > 1-in-100yr. | 'These calculations are based on Engineering Hydrology by E.M.Wilson (4th Edition)' ... 'The approach is also similar to BRE Digest 365 Soakaway Design' ... 'These are based on the Wallingford Procedure and the Flood Studies Report' — no mention of GDSDS, GDRCoP, FSU or Fingal-specific design rainfall. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Cl 2309 - SurfaceWaterAttenuation.xlsx | CS_DESIGNER | OPEN
S-020 | HIGH | C&S | STRUCTURAL_SAFETY | 50004 - RC Roof Slab.pdf; Section L; RC Roof Cantilever detail | Section L (cantilever connection), External leaf support note | I.S. EN 1992-1-1 (thermal-break connector design); I.S. EN 845-1 (Masonry support angles); BBA / ETA approval framework for proprietary products; manufacturer Schöck Isokorb DTA. | Drawing names 'Schöck Isokorb or similar approved' for the cantilever thermal break and 'IG Masonry support or equivalent approved' for the 200 mm cavity / 8 kN brick-leaf support. Both are proprietary products requiring named-type designation (Isokorb K, KS, KXT etc.; IG model number) to size the moment & shear capacity. As drawn, the load is stated as 8 kN per linear metre? per fixing? — ambiguous. The contractor will price the cheapest equivalent which may not meet the actual moment/shear induced by the slab cantilever, and the thermal performance (EE finding) is also affected. No fire-rating noted on the supports for compartment-line crossings. | Designate specific product types (e.g. Isokorb K35-CV35-V8-H180 or as designed) on the drawing with stated design moment (kNm/m) and shear (kN/m) so 'equivalent approved' submissions can be properly assessed. Confirm fire rating of supports where they cross compartment walls. Coordinate with arch on cavity dimension and with EE on Ψ-value (linear thermal transmittance). | 'Thermal brake with cantilever connectors for moment and shear force stresses Schock Isokorb or similar approved' and 'External leaf support suitable for 200mm cavity and 8KN load IG Masonry support or equivalent approved'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50004 - RC Roof slab.pdf | CS_DESIGNER | OPEN
X-003 | HIGH | FIRE/COORDINATION | COMPLIANCE | Electrical Specification §12.01-12.03 + Fire Compliance Report Stage 2(c) Condition 2 | Elec Spec line 3387 (3218 reference) vs FSC Condition 2 (IS 3218:2024) | FSC granted 19/08/2025 Condition 2 (compliance with IS 3218:2024); IS 3218:2024 §6 (Category L1/L2/L3/M designation must be explicit); BS 9999 §17 (fire alarm system design) | FSC Condition 2 imposes IS 3218:2024 but Electrical Specification line 3387 cites 'I.S 3218: 2013'. IS 3218:2024 introduced material changes in zoning, voice alarm thresholds, multi-sensor requirements and false-alarm management — tenderers pricing to the 2013 edition will not include the cost delta. Specification also states 'L2/L3 fire detection and alarm system' — these are TWO DIFFERENT CATEGORIES under IS 3218 and the FSC requires a single defined category. Mechanical/Architectural coordination point: IS 3218:2024 §6 also drives heat-detector placement in the kitchen above the cooker hood and interlock with the kitchen extract suppression system (FSC Condition 5) — this interlock is not specified in either pack. | ER to instruct T5 Engineering (M&E) to (a) reissue Electrical Specification Section 12.0 referencing 'IS 3218:2024 throughout' with explicit single Category designation (recommend L2 for healthcare day-care occupancy with sleeping not envisaged), (b) add cause-and-effect matrix showing kitchen-hood detector → suppression interlock → gas-shutoff valve → fire alarm panel signal, (c) coordinate this with Mech Spec to ensure mechanical scope includes the suppression system to IS EN 16282-7 (currently silent — see X-004). | Elec Spec line 3387: 'proposed scheme is in full compliance with I.S 3218: 2013, the manufacturer's recommendations and this specification' … Elec Spec line 3362: 'The overall building will be provided with an L2/L3 fire detection and alarm system' … FSC Condition 2: '[fire detection per] IS:3218:2024' | Electrical Specification §12.01-12.03 + Fire Compliance Report Stage 2(c) Condition 2 | ER — T5 Engineering (M&E Designer) via Employer's Representative | OPEN
X-005 | HIGH | FIRE/COORDINATION | COMPLIANCE | Architectural Spec Q37 Green roof; Civil/Structural Spec; Electrical Spec §13.0 PV Installation; Arch Roof Plan AR-11002; C&S Roof Plan 11003 | Arch Spec line 13135-13190 (Bauder green roof); Elec Spec line 4865+ (PV); FSC Conditions 6 & 7 | FSC Conditions 6 & 7 (granted 19/08/2025); BS 8616:2019 (green roofs); GRO Green Roof Code of Practice 2014; DCLG/MHCLG 'Fire performance of green roofs and walls' 2013; FPA RC62 + NFPA 1 §11.2 PV; TGD-B Vol 2 (2024) §B4 (external fire spread — roofs); EN 13501-5 (roof external fire performance Broof(t4)) | Architectural Spec Q37 specifies Bauder Extensive Sedum Blanket but is SILENT on the three Condition-7 standards (BS 8616:2019, DCLG 2013, GR Code of Practice 2014). Electrical Spec §13 cites FPA RC62, NFPA 1 §11.2 and MCS/ECA — only 3 of the 4 standards required by FSC Condition 6 (the 4th — typically the EN 13501-5 / IEC 61730 / Eurocode wind-uplift cross-reference — is missing). C&S Spec contains NO mention of green roof or PV saturated dead load or wind-uplift design for either system; structural Roof Plan 11003 must be coordinated with the 500 mm firebreak between PV array and roof edge required by RC62 and with sedum saturated load (~120 kg/m² wet) plus PV array dead+uplift. Three-way coordination gap (Arch / C&S / Elec) on a single roof. | Pre-tender: (1) Architect to amend Q37 to incorporate the three Condition-7 standards explicitly with 'compliance with' language. (2) T5 (Elec) to add the missing fourth Condition-6 PV standard (recommend explicit reference to IEC 62446 + EN 13501-5 Broof(t4) for combined PV+green roof). (3) Kavanagh Mansfield (C&S) to confirm on the Roof Plan structural calculations the saturated green-roof load case AND the PV array load case AND the combined 500 mm firebreak set-out. (4) All three to coordinate on a single Roof Coordination Drawing showing: PV array footprint, 500 mm perimeter firebreak (gravel/paving), sedum zone, drainage outlets and inverter location relative to fire-officer-accessible isolation point. | Arch Spec Q37 line 13135: '130 Extensive green roof systems … Product reference: Bauder Extensive Sedum Blanket System' — no reference to BS 8616, DCLG 2013 or GR Code of Practice 2014. Elec Spec line 4886-4889: '"RC62 : Recommendations for Fire Safety with Photovoltaic Panel Installation" published by FPA/RISC Authority. NFDA 1 (Fire Code) Section 11.2 for PV Systems. MCS/ECA's Guide to Installations of PV Systems.' — only 3 of 4 standards. C&S Spec grep for 'green roof' / 'sedum' / 'PV' returns no design loading references. | Architectural Spec Q37 Green roof; Civil/Structural Spec; Electrical Spec §13.0 PV Installation; Arch Roof Plan AR-11002; C&S Roof Plan 11003 | LEAD_DESIGNER — Rhatigan (Lead) coordinating Kavanagh Mansfield + T5 | OPEN
X-006 | HIGH | FIRE/COORDINATION | COMPLIANCE | Architectural Internal Door Schedule AR-40001; Ironmongery & Access Control AR-40010; Fire Compliance Report §9 (Cause & Effect) | Therapy Room doors D0.021/0.022/0.023/0.025/0.029 (Set 10A); Corridor doors D0.006/D0.024 (Set 01); Fire Report Note 10 (BGU rule) | IS EN 13637:2015 (electrically controlled exit systems for use on escape routes); BS 7273-4:2015 (actuation of release mechanisms for doors); TGD-B Vol 2 (2024) §B1.5 (means of escape — locking devices); FSC Condition 2; HIQA National Standards for Disability Services Theme 1 (rights — including freedom of movement) | Cause-and-effect agreed 16/09/2025 (Fire Report §9) but Fire Report Note 10 states 'BGUs can be removed from therapy room doors provided final exit doors from these rooms are always available for escape AND provided with a simple fastening for escape compliance. Any therapy room or other room WITHOUT a final exit directly to outside will require a BGU.' The Door Schedule shows D0.021-D0.029 therapy rooms with Set 10A 'Access Control to both sides. No BGU required - escape provided from external door' — but the package does NOT provide an FSC-compliant marked-up plan demonstrating that EACH of these therapy rooms has a verified direct external escape route AND that the external escape door has the simple-fastening compliance. If any therapy room is locked from the corridor side AND its external door is found at handover to lack the IS EN 1125/179 compliant simple fastening, the building fails Part B at first inspection. Healthcare overlay: HIQA will require that a service user with mobility impairment can always self-egress — the BGU-bypass strategy must be tested for the disabled user population, not just an able-bodied evacuee. | Pre-tender: Architect to issue a Therapy Room Egress Compliance Drawing overlaying (a) each therapy room door (with access control), (b) the corresponding external escape door + IS EN 1125 panic / EN 179 emergency exit ironmongery reference, (c) the protected escape route from each therapy room to the place of safety. ORS Fire to formally sign this drawing. Reference IS EN 13637 cause-and-effect in the Elec Spec for the access control system + 15-second time delay confirmation already noted on Set 01 corridor mag-locks. PSDP to add to risk register: 'Access control system commissioning + simple fastening verification' as a pre-occupation gate. | Fire Report Note 10: 'It was noted that the Green BGU's for access control to the internal doors to the therapy rooms can be removed provided the final exit doors from these rooms are always available for escape purposes and provided with a simple fastening for escape compliance. Any therapy room or any other rooms for that matter without a final exit directly to outside will require a BGU.' Door Schedule D0.021 THERAPY ROOM Set 10A: 'Access control to both sides. No BGU required - escape provided from external door.' [repeated for D0.022/0.023/0.025/0.029] | Architectural Internal Door Schedule AR-40001; Ironmongery & Access Control AR-40010; Fire Compliance Report §9 (Cause & Effect) | ARCH_DESIGNER — Rhatigan + ORS Fire (joint sign-off) | OPEN
X-007 | HIGH | FIRE/COORDINATION | CONTRACT | Whole pack — BCAR Ancillary Cert allocation; PW-CF5 Schedule of Designers | Architectural / C&S / M&E / Electrical / Fire specs — designer naming | SI 9/2014 Building Control (Amendment) Regulations 2014 Reg 9 (Design Certifier) + Code of Practice for Inspecting and Certifying Buildings and Works §2.4 + Annex A (named designer of each element required); PW-CF5 (Employer-Designed) — design responsibility sits with Employer's Design Team; Code of Practice Annex A Design Cert template requires the designer of every element to be named. | Pack is procured as PW-CF5 Employer-Designed, meaning EVERY Ancillary Cert at completion sits with the Employer's Design Team (Rhatigan / Kavanagh Mansfield / T5 / ORS). However, the pack does NOT include a Schedule of Designers / BCAR Ancillary Cert allocation matrix naming the chartered designer responsible for: Substructure, Superstructure, Roof (Arch + C&S joint), External walls + Fenestration, Internal walls + Doors, Finishes, Drainage (split between C&S surface water and Mech internal foul), HVAC, Plumbing, Electrical, Fire Detection & Alarm, Emergency Lighting, PV system, Lifts/Hoists (HBN 00-09 hoist track if present), Fire Safety Design, Access Control / Mag-locks (IS EN 13637 system). At handover, missing Ancillary Cert authorship will block the Statutory Cert of Compliance on Completion. C&S Spec line 173-182 references 'Assigned Certifier' but the Employer has not been confirmed in the pack — the BCAR triangle (Owner / Assigned Certifier / Designers) is not closed. | Pre-tender: ER to issue a 'BCAR Designer Allocation Matrix' as Tender Volume 2 Schedule, listing each element from Code of Practice Annex A against the named individual chartered professional (RIAI / IStructE / Engineers Ireland / CIBSE) responsible. Confirm Assigned Certifier appointment (RIAI-registered Architect or chartered Engineer). Ensure PSDP appointment is also named (SI 291/2013 Reg 9). Include Designer Declarations as Schedule to PW-CF5 so post-contract the designer cannot disown ancillary scope. | C&S Spec line 173-177: 'The contractor shall notify the Engineer of dates for inspection, as well as the Assigned Certifier. … The Assigned Certifier shall mean the person engaged by the client to certify the [works].' Elec Spec line 2510: 'Contractors are required to provide BCAR Design Certs for all suspension systems.' — sole BCAR reference in Elec spec, no whole-discipline allocation. Architectural Spec line 6765: 'All Certificates, DoP's, etc. are to be issued to the Employers Representative & Assigned Certifier' — Assigned Certifier not named in pack. | Whole pack — BCAR Ancillary Cert allocation; PW-CF5 Schedule of Designers | ER — Employer's Representative (to confirm AC + designer allocation) | OPEN
X-008 | HIGH | FIRE/COORDINATION | OPERATIONAL | Whole pack — Disabled Refuge / Means of Escape for Disabled Persons | Elec Spec lines 5967-5973 (Disabled Refuge System); Arch Spec (silent); GA Plan AR-11001 (no refuge zones marked) | TGD-B Vol 2 (2024) §B1.1.5 (provision for persons with disabilities); BS 9999:2017 §46 (refuge areas); BS 5588-8 (now withdrawn but principles retained); HIQA National Standards for Disability Services Theme 5 (Safe Services); SI 291/2013 (PSDP — emergency preparedness in design) | Electrical Specification lines 5967-5973 instruct 'Complete supply, installation and testing of Disabled Refuge System' (intercom). BUT the Architectural Spec is silent on Refuge designation, and GA Plan AR-11001 grep returns no 'refuge' callout. This is a healthcare day-care building expressly serving service users with intellectual and physical disability — every escape route must terminate at a designated refuge OR a direct final exit accessible to wheelchair users. As single-storey, the building may avoid mandatory upper-storey refuge, but the External Stair (drawing 50007) infers a level change that creates a refuge requirement. Coordination failure: Electrical bidder will price refuge intercoms but they will have nothing on the wall plan to mount to and no clear architectural zone designation. | Pre-tender: Architect to (a) confirm in writing whether building is genuinely single-storey at-grade throughout (with reference to External Stair purpose); (b) if any level change > 0 risers separates a wheelchair-occupiable zone from the final exit, designate a Refuge Area on AR-11001 with the BS 9999 minimum 800 mm × 1400 mm clear area; (c) coordinate refuge intercom point location with T5 Elec at the Refuge designation. ORS Fire to confirm evacuation strategy is documented — simultaneous, phased, or progressive horizontal — and the strategy is consistent with the day-care user population. Add a PEEP (Personal Emergency Evacuation Plan) regime to O&M to be operated by the Building Owner under HIQA. | Elec Spec line 5967-5973: 'Complete supply, installation and testing of Disabled Refuge System'. Arch Spec grep for 'refuge' / 'disabled refuge' returns 0 hits. GA Plan AR-11001 fire legend lists 60-min / 30-min walls and rated glazing but no Refuge designation. | Whole pack — Disabled Refuge / Means of Escape for Disabled Persons | ARCH_DESIGNER — Rhatigan + ORS Fire | OPEN
X-009 | HIGH | FIRE/COORDINATION | COMPLIANCE | Compartment wall service penetrations — Mech Spec + Elec Spec + Arch Fire Stopping Sheets 1-5 | AR-59001/59002/59003/59004 (Fire Stopping Details); Mech ductwork drawings 1743_55_xx; Elec containment drawings 1743_68_xx; FSC Condition 3 | TGD-B Vol 2 (2024) §B3.5 (Compartmentation — penetrations §3.5.13 / firestopping §3.5.14); BS EN 1366-3 (penetration seals); BS EN 1366-4 (linear joints); EN 1366-8 (fire dampers — re-classification); FSC Condition 3 | FSC Condition 3 requires compartment walls to TGD-B 2024 with explicit reference to §3.5.13 (penetrations) and §3.5.14 (firestopping). Architectural Fire Stopping detail sheets are titled AR-59001 (Sheet 1), 59002 (Sheet 2), 59003 (Sheet 3) and 59004 ('Sheet 5'). SHEET 4 IS MISSING from the pack (issue sheet jump 3 → 5). Mech & Elec service routes through compartment walls are not cross-referenced to specific fire-stopping detail numbers — there is no penetration schedule (typically a 'Service Penetration Schedule' listing each duct/cable bundle/pipe penetration, host wall fire rating, EN 1366 third-party-tested solution and Declaration of Performance). Mech Spec also does not specify fire dampers in ductwork crossing compartment lines (e.g. kitchen extract ductwork through KITCHEN FD60S compartment wall). Three-discipline gap. | Pre-tender: (1) Architect to confirm and reissue AR-59004 as 'Sheet 4' or amend issue sheet to declare 'AR-59004 Sheet 5 — note Sheet 4 not used'. (2) Rhatigan, T5 Mech and T5 Elec to jointly produce a Service Penetration Schedule mapping every mech duct / elec containment / plumbing pipe crossing a 30-min or 60-min compartment wall to (a) the host wall type per AR-15001, (b) the proprietary penetration seal (third-party tested), (c) the relevant Fire-Stopping detail sheet. (3) Mech Spec to add Fire Damper schedule for any ductwork crossing compartment walls. (4) ORS Fire to sign the Service Penetration Schedule as 'reviewed for Part B compliance'. | Fire-Stopping sheets in pack: AR-59001 'Sheet 1', AR-59002 'Sheet 2', AR-59003 'Sheet 3', AR-59004 'Sheet 5' — Sheet 4 absent. AR-59003 text extract: 'Pipe Collar — Plastic Pipe — 1: Typical Pipe Collar detail through concrete floor' — no schedule of where this applies. Mech Spec grep for 'fire damper' / 'EN 1366-2' returns no kitchen extract-specific entries. | Compartment wall service penetrations — Mech Spec + Elec Spec + Arch Fire Stopping Sheets 1-5 | ARCH_DESIGNER — Rhatigan (lead) + T5 Mech + T5 Elec | OPEN
X-010 | HIGH | CROSS-DISCIPLINE | OPERATIONAL | Architectural Therapy / Sensory / Activity room specs; M&E Specs | Arch Spec acoustic partition entries; Sensory Room finishes; therapy room ironmongery; Mech HVAC zoning | BB93 (Building Bulletin 93 — acoustic design of schools — applied by HIQA analogy for SEN environments); HTM 08-01 (Acoustics); HBN 00-09 / 00-10 (infection control + sanitary assemblies); HIQA National Standards for Disability Services Theme 7 (Health and Development — environmental design); HSE PCM Healthcare Design Standards | WT4 partition achieves 53 RwdB sound insulation — appropriate between therapy rooms — but no design verification that the doors (T2 with Set 10A) achieve a coordinated acoustic seal (door schedule shows 'Acoustic Seals: Yes' on FD60S only, blank on therapy room T2 doors). HVAC supply to adjacent therapy rooms may flank-transmit through ductwork — Mech Spec is silent on cross-talk attenuators between therapy room supplies. Sensory Room (Room 0.10 / 0.27) requires tunable lighting + reduced acoustic reverberation + no shadow gaps — Elec Spec lighting clauses do not call out DALI tunable-white scenes for Sensory Rooms specifically. Cross-discipline gap that will surface during HIQA pre-registration inspection. | Pre-tender: (1) Architect to add door acoustic seal column to therapy room T2 doors AND specify a minimum door-set Rw rating (suggest 35 dB Rw to align with HTM 08-01). (2) T5 Mech to add cross-talk attenuators (XTA) between therapy supplies and add to Mech Spec ductwork section. (3) T5 Elec to specify DALI tunable-white scene-set for Sensory Room luminaires with named controller (e.g. CASAMBI / DALI-2 D4i). (4) Architect to confirm sensory room internal finishes are non-reflective, no shadow gaps and infection-control compliant per HBN 00-09. (5) PSDP/ER to confirm HIQA pre-registration inspection regime to ensure these design intents survive contractor value engineering. | Arch Wall types: 'WT4 Partition Wall Type 4 … Sound Insulation Rating: 53 RwdB' — but Door Schedule AR-40001 'Acoustic Seals' column populated only for D0.009 KITCHEN FD60S; D0.021-029 THERAPY ROOM T2 doors show 'Acoustic Seals: Yes' generically without dB rating. Mech Spec grep for 'cross-talk' returns 0 hits. Elec Spec line 3193+ on lighting controls references absence detection / push-dimming but does not call out tunable-white scenes for Sensory Rooms. | Architectural Therapy / Sensory / Activity room specs; M&E Specs | LEAD_DESIGNER — Rhatigan (lead) + T5 Mech + T5 Elec | OPEN
A-004 | MEDIUM | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Drawing Register | Section heading '3000 SECTIONS' | Internal numbering convention | Section heading shows '3000' but should be '30000' to match 5-digit hierarchy used elsewhere in the register (10000, 11000, 13000, 15000, 17000, 20000, 25000, 31000…). Inconsistent hierarchy may confuse CDE filing. | Correct register section heading to '30000 SECTIONS'. | Register p.1: '3000 SECTIONS' immediately preceding drawings 11606-XX-ZZZ-DR-RHA-AR-30001/30002. | 11606-RG-RHA-AR-0001 Drawing Register p.1 | ARCH_DESIGNER | OPEN
A-005 | MEDIUM | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Drawing Register | Room 0.09 Accessible WC and Room 0.32 Meeting & Consultation | Register completeness | Register page 2 omits drawing for Room 0.09 (between 0.08 and 0.10) but file inventory shows 60009 present in pack. Register layout corruption — room 0.32 layout split across two rows. Pack reality vs register state drift. | Reissue register page 2 with all room layout drawings consistently listed including 0.09 Accessible WC. | Register p.2 jumps from '11606-XX-L00-DR-RHA-AR-60008 0.08 - Group Therapy Room' to '11606-XX-L00-DR-RHA-AR-60010 0.10 - Sensory Room' — 60009 absent. File '60009- 0.09 Accessible WC.pdf' confirmed present in pack. | 11606-RG-RHA-AR-0001 Drawing Register p.2 + pack manifest | ARCH_DESIGNER | OPEN
A-006 | MEDIUM | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Drawing Register | Status code P08-S vs declared issue purpose 'T' (Tender) | BS EN ISO 19650-2 §5.3.2 (status code use) | All drawings carry status 'P08-S' (typically Preliminary, suitability code S). Register issue list shows 'T' (Tender) for all recipients. P08-S Preliminary is NOT a tender-issue status code. Recipients may treat drawings as not-for-tender. | Update all drawing status codes to a tender-issue suitability (e.g. S4 or A1 per ISO 19650 conventions used in Ireland). Reissue register to confirm tender purpose. | Register p.1-2: Every drawing carries 'P08-S'. Legend p.2: 'T - tender' listed as issue purpose. | 11606-RG-RHA-AR-0001 Drawing Register p.1-2 | ARCH_DESIGNER | OPEN
A-023 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section P12 'Fire-stopping systems' | TGD-B Vol.2 (2024) §3.5.7 Accommodation of services in compartment walls and Appendix A; FSC Cond. 3 (services in compartment walls per 3.5.7 and Appendix A); BS 9999:2017 §32; ASFP Red Book. | P12 specifies generic 'Contractor's choice' for every fire-stopping product including pipe collars, mineral wool batts, intumescent mastic. There is NO call-up of TGD-B 2024 Appendix A penetration-detail family, no requirement for a third-party-accredited installer scheme (FIRAS / IFC), and no commissioning/inspection protocol identifying who signs off fire-stopping per BS 9999 §32. Result: site fire-stopping installed to lowest cost, no audit trail, Assigned Certifier unable to sign Ancillary Cert. | Strengthen P12 to require: (a) third-party-accredited installer (FIRAS or IFC equivalent); (b) penetration-by-penetration register issued as Built Drawings; (c) all detail families to be benchmarked against TGD-B 2024 Appendix A diagrams; (d) Fire Stopping Sign-Off Sheet executed by installer's competent person, witnessed by Assigned Certifier or his delegate; (e) photographic record per BS 9999 §32. Cross-ref P12/620 'Workmanship'. | P12/330 Flexible intumescent gap sealer Manufacturer: Contractor's choice / Product reference: Contractor's choice. P12/338 Intumescent mastic Manufacturer: Contractor's choice. P12/345 Intumescent pillows Manufacturer: Contractor's choice. [No installer-accreditation requirement; no penetration register requirement; no Appendix A reference] | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.156-159 (P12) | ARCH_DESIGNER | OPEN
A-024 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section L30/102 'Design' and L30/107 'Completion of design' | TGD K (Stairways, Ladders, Ramps and Guards) 2014; the Irish Building Regulations apply BS 5395-1 and TGD K, NOT 'Building Regulations (Eng) Approved Documents K and M'. | L30/107.2.1 cites 'Building Regulations (Eng) Approved Documents K and M' (English Approved Docs), not TGD K and TGD M. UK Approved Docs differ materially from Irish TGDs (rise/going, handrail height, glazing protection differ). Tender will be priced to wrong code; Assigned Certifier cannot sign for compliance. | Amend L30/107.2.1 to: 'Standard: To Irish Building Regulations Technical Guidance Document K (current edition - 2014 as amended) and Technical Guidance Document M (current edition - 2022). UK Approved Documents shall not apply.' Audit all other 'Approved Document' references in the Arch Spec and convert to TGD nomenclature. | 107 Completion of design 1. Description: Concrete stairs 2. Requirement: Complete the detailed design ... 2.1. Standard: To Building Regulations (Eng) Approved Documents K and M | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.89 (L30/107) | ARCH_DESIGNER | OPEN
A-025 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section L30/102 'Design' | BS EN 1991-1-1 (imposed loads); IS EN 1991-1-1 Irish National Annex (specifies imposed loads for stair use category C3/C4 in assembly/healthcare buildings); BS 6399-1:1996 superseded. | L30/102 specifies 'Type of activity/occupancy category to BS EN 1991-1-4 (Domestic and residential activities)'. BS EN 1991-1-4 is the WIND code, not the imposed load code. The correct Eurocode is BS EN 1991-1-1, and a Day Care Centre is occupancy Category C3 (areas without obstacles for moving people - assembly) not 'Domestic and residential'. Stair will be designed to ~2.0 kN/m^2 instead of required 4.0 kN/m^2. Structural under-design. | Amend L30/102 to: 'Type of activity/occupancy category to BS EN 1991-1-1 Table 6.1: Category C3 (areas where people may congregate, including therapy and assembly use). Imposed load 4.0 kN/m^2 minimum. Stair handrail and balustrade design horizontal line load to BS EN 1991-1-1 Table 6.12: 1.5 kN/m. Co-ordinate with Structural Engineer.' | 102 Design ... Type of activity/occupancy category to BS EN 1991-1-4 (Domestic and residential activities). | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.89 (L30/102) | ARCH_DESIGNER | OPEN
A-026 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section L40/250 (Bead-fixed single glazing internal doors and screens) | TGD K 2014 §K4 (glazing in critical locations); BS 6262-4:2018 §6 Critical Locations; BS EN 12600:2002 (impact classification). | L40/250 names 'Clear toughened glass' for internal door/screen glazing but no impact classification (Class 1B1 minimum per BS 6262-4 for critical locations) and no manifestation. L40/165 calls for heat-soaking only to 1500mm FFL without distinguishing critical location. For a Day Care with vulnerable adults, all glazing in critical locations should be safety-rated and manifestated to BS 8300-2 §9.4. | Add to L40/250 sub-clause 'Performance': 'Impact classification: BS EN 12600 Class 1B1 minimum (toughened or laminated). Manifestation: in accordance with BS 8300-2 §9.4 - two contrasting bands 150mm thick at 850-1000mm and 1400-1600mm above FFL on all clear glazed door leaves and adjacent screens.' Add manifestation sub-clause to L40/370 (external). | 250 Bead-fixed single-glazing 1. Description: Internal doors and screens 2. Pane material: Clear toughened glass [no impact class, no manifestation requirement] | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.94 (L40/250) | ARCH_DESIGNER | OPEN
A-027 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section L20/430 (Internal wood doorsets) and L20/115 (Fire-resisting doorsets) | TGD-B Vol.2 (2024) Appendix B Table B1 (fire doors require certified evidence per BS EN 1634-1 or BS 476-22); BS EN 16034 + BS EN 14351-1/-2; FSC Cond. 3. | L20/430.10.1 'Fire resistance: Refer to door schedule' is acceptable but L20/115.3 conflates 'Specified values should not be a combination of both standards' yet the schedule uses 'FD30S/FD60S' (BS 476 nomenclature) while L20/115 invokes BS EN 1634-1 (EI class nomenclature). Internal Door Schedule 40001 mixes 'FD60S' and 'FD60S' in adjacent columns for D0.009 (Kitchen). Smoke classification 'S' must be Sa (ambient) - this is not specified. | Standardise on BS EN nomenclature: e.g. 'EI 30-Sa for FD30S; EI 60-Sa for FD60S' through both spec L20/115 and Schedule 40001. Clarify what 'S' means (Sa ambient smoke). Add UKCA/CE marking requirement to be evidenced via DoP for each doorset. Add 'Cold-smoke seal' acceptance test reference BS 476-31.1 (already cited at L20/430.10). | L20/115.3: 'Specified values should not be a combination of both standards.' L20/430.10: 'Smoke leakage: Smoke: BS EN 1634-3: 2004 & BS 476-31.1: 1983. Refer to door schedule.' Schedule 40001 D0.009 shows 'Fire Rating: FD60S' and 'Fire Rating Acoustic Seals: FD60S'. | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.83-84 (L20/115, L20/430); 11606-XX-XXX-SH-RHA-AR-40001 row 188 | ARCH_DESIGNER | OPEN
A-028 | MEDIUM | ARCHITECTURAL/COORDINATION | DOCUMENT_HYGIENE | Architectural Works Specification & Ironmongery Schedule 40010 | P21 'Ironmongery'; Ironmongery & Access Control Plan & Schedule 40010 | IS EN 13637:2015 Electrically controlled exit systems; BS EN 1125:2008 Panic exit devices; BS EN 179:2008 Emergency exit devices; Fire Report Note 9 (16/09/2025) - 'Types of systems and ironmongery are yet to be approved'. | Fire Report Note 9 expressly states ironmongery 'yet to be approved'. P21/10 pushes the Ironmongery Schedule onto the Contractor: 'Quantities and locations of ironmongery: Contractor to prepare ironmongery schedule based on the architectural drawings.' This is incompatible with Fire Cert delegated requirements (cause-and-effect, maglock release timing per IS EN 13637, BGU positioning). The Contractor is being asked to do the Designer's job for safety-critical kit. (See F-002 - parent Fire-side log.) | Architect / Fire Engineer to issue Final Ironmongery Schedule for Tender prior to 10-Jun-2026 close, including: Set-by-Set descriptors, EN classification, lock case, closer Power Size, hinge grade, panic/emergency device certification, maglock (Grade 1) release method, time delay value (15s confirmed per Fire Report), cause-and-effect interface with FDAS. Remove P21/10 'Contractor to prepare ironmongery schedule'. Issue as Tender Addendum. | P21/10 Quantities and locations 1. Quantities and locations of ironmongery: Contractor to prepare ironmongery schedule based on the architectural drawings. ... Fire Report Note 9: 'Types of systems and ironmongery are yet to be approved.' | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.161 (P21/10); 22481-Stage 2C Report-Part B Compliance.pdf p.4 | ARCH_DESIGNER | OPEN
A-029 | MEDIUM | ARCHITECTURAL/COORDINATION | COMPLIANCE | Architectural Works Specification | Section L20/610 'Fire Curtain' | FSC Cond. 5 (kitchen suppression IS EN 16282-7); BS EN 1634-1; BS 7346-3:2013 (smoke and heat control - including modifications to BS 7346-3:1990 cited in spec). | L20/610 specifies a 60-minute Fire Curtain to the Kitchen referencing 'BS 7346 - Part 3: 1990, BS 476 - Part 6: 1989 and Part 22: 1987'. BS 7346-3:1990 is superseded by BS 7346-3:2013, BS 476-22:1987 is still current but UK practice has moved to BS EN 1634-1. Kitchen also has D0.009 FD60S leaf - duplication of fire separation. The fire curtain plus FD60S double-provision should be confirmed with the Fire Engineer that both are required (curtain typically used in lieu of an opening, not in addition). Cause-and-effect for the curtain (link to FDAS, UPS, manual override) is not specified. | Update L20/610 standards to BS 7346-3:2013 and BS EN 1634-1. Clarify with Fire Engineer whether the curtain is required when D0.009 FD60S is closed. Add cause-and-effect to align with FSC Cond. 5 (kitchen suppression interfaces with FDAS, gas isolation, mechanical extract shutdown, curtain deployment). | 610 Fire Curtain 1. Description: 60 minutes fire resisting curtain to Kitchen ... 3. Standard: To BS 7346 - Part 3: 1990, BS 476 - Part 6: 1989 and Part 22: 1987, BS EN 1634-1: 2008. | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.85-86 (L20/610) | ARCH_DESIGNER | OPEN
A-030 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section L20/180 (Strength class) & L20/170 (Ironmongery for fire doors) | BS EN 1906:2012 (lever handles), BS EN 1154 (controlled door closers); DD 171 is withdrawn since 2007; current standard is PD 8300 / BS 8300-2. | L20/180 cites 'DD 171' (Draft for Development on door durability) which has been WITHDRAWN by BSI since 2007 and replaced by performance criteria in BS EN 1191 / BS EN 12400. Tendering against a withdrawn standard creates Compensation Event risk. | Replace 'DD 171' with: 'BS EN 1191:2012 (mechanical fatigue) and BS EN 12400:2002 (cycles category)'. Re-issue strength categories using current Euroclass durability ratings (D1-D8 to BS EN 1191; cycle categories to BS EN 12400). | 180 Strength class or category of duty for door ironmongery 1. Requirement: To DD 171 | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.161 (P21/180) | ARCH_DESIGNER | OPEN
A-031 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section P21/315 (External door hinges) | BS EN 1935:2002 (hinge classification); BS EN 1670:2007 corrosion resistance. | P21/315 specifies external door hinge 'Corrosion resistance: 1' to BS EN 1935. Grade 1 is the LOWEST corrosion class (= mild conditions). External doors in an Irish climate (BS EN 1670 exposure grade 4 to 5) require Grade 5 (high) or Grade 4. Hinges will rust within warranty period, causing door binding and possible escape route obstruction. | Amend P21/315 sub-clause 3.5: 'Corrosion resistance: 4 (high)' or Grade 5 if marine exposure modifier applies. Co-ordinate with door supplier Polyester Powder Coat 25-year guarantee. | 315 Performance specification for single-axis door hinges 1. Description: External Doors ... 3.5. Corrosion resistance: 1 | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.161-162 (P21/315) | ARCH_DESIGNER | OPEN
A-033 | MEDIUM | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Works Specification | Section P10/410, P10/420, P10/432 (Cavity barriers) | TGD-B Vol.2 (2024) §3.6 Cavity barriers - locations, type (EI 30 or EI 60 depending on building height/use), maximum unobstructed dimension 20m vertical / 10m horizontal in concealed roof spaces above corridors; FSC Cond. 4 (cavities per TGD-B 2006 Reprint 2020 §3.3 - inconsistent with TGD-B 2024 for the main building). | P10/410, /420, /432 all specify cavity barriers as 'EI 60'. TGD-B 2024 §3.6 sometimes accepts EI 30 in this building class - over-specifying drives cost. Conversely the FSC Cond. 4 directs TGD-B 2006 Reprint 2020 (not 2024) for cavities. The Arch Spec must align with the FSC condition. Mixed citation creates dispute risk and unclear acceptance criteria. | Reconcile P10/410-/432 with FSC Cond. 4: cite 'TGD-B 2006 Reprint 2020 §3.3' as governing for cavity barriers, with location and type per Fire Strategy drawings. Confirm EI 30 vs EI 60 by zone. (See F-001 for parent.) | P10/410 Flexible cavity barriers ... 3. Fire resistance rating: To BS EN 13501-2, EI 60. P10/420 Sleeved mineral wool small cavity barriers ... 3. Fire resistance rating: To BS EN 13501-2, EI 60. P10/432 Cavity barriers ... 2. Fire resistance rating: To BS EN 13501-2, EI 60. | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.151-152 (P10/410, 420, 432) | ARCH_DESIGNER | OPEN
A-034 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section N14 General internal signage systems (clauses 110/112) | TGD M 2022 §1.4 (Wayfinding and signage); BS 8300-2:2018 §9.2 Signs and information; NDA 'Building for Everyone' Booklet 4 §4.3 Tactile and Braille requirements. | N14 has multiple sub-types (D, F, G, I, H, I1, I2, I3) all defaulting to 'Refer to current HSE Signage Manual'. The HSE Signage Manual is a brand standard; it does not constitute compliance with TGD M, BS 8300-2 or NDA Booklets for tactile, Braille, contrast, mounting height, font case (sentence case lower-cased per BS 8300-2). No clauses for tactile/Braille font height, character size, LRV contrast 30 minimum, mounting height 1400-1700mm, signage at door push side at 50mm from leading edge per BS 8300-2 §9.2. | Add a sub-clause 'Accessibility compliance' to each N14 sign type: 'In addition to HSE Signage Manual, all signage shall comply with BS 8300-2:2018 §9.2 including: tactile relief 1-1.5mm; Grade 1 Braille below tactile text; LRV contrast 30 minimum between text and background; sans-serif font; mounting height 1400-1700mm; door push-side signage 50mm from leading edge of door.' | 110 Signage system Type D ... Pantone 561C - Refer to current HSE Signage Manual / Size: Refer to current HSE Signage Manual / Background colour: Refer to current HSE Signage Manual | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.137-140 (N14/110, /112 multiple types) | ARCH_DESIGNER | OPEN
A-035 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Architectural Works Specification | Section N25 'Permanent access and safety equipment' | BS 7883:2019 (selection and installation of anchor devices conforming to BS EN 795); BS 8437:2005+A1:2012 (selection and use of personal fall protection); Safety Health and Welfare at Work (Work at Height) Regulations 2006. | N25 specifies a cable fall-restraint system to roof but no Roof Access Plan reference, no User Manual / Method Statement output, no annual inspection clause beyond generic N25/810 'Service/maintenance'. PV array installation and Bauder green roof maintenance both require defined safe access. Operator risk and PSCS liability transfer issue at handover. | Add to N25/810: 'Provide certified user training for Employer's facilities team (NSAI/IOSH equivalent) prior to handover, with first annual statutory inspection date scheduled within Safety File. Issue a Roof Access Plan reference (drawing 11002) cross-coordinated with PV array and green roof maintenance zones.' | 210 Personal fall protection equipment 1. Description: Stainless steel anchored cabled fall restraint system ... 6. Overall system length: Refer to 11002 Roof Plan [no User Manual, no training, no first inspection date] | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.143-145 (N25) | ARCH_DESIGNER | OPEN
A-110 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Internal Finishes Schedule — Sensory Rooms | Drawing 40009 rows 0.10 and 0.27 | HBN 00-09 §4 wall protection in clinical/therapy spaces; HSE design guidance for sensory environments (impact, ligature, wipeability) | Sensory Rooms 0.10 (6.76 m²) and 0.27 (10.06 m²) walls specified only as 'Washable matt emulsion paint'. No impact-resistant wall protection to dado, no acoustic panel callout for environmental control. Users with sensory needs may strike walls — damage/injury risk. Sensory environment performance not assured. | Add impact-resistant PVC wall protection (e.g. Yeoman Shield 1200mm dado) to Sensory Rooms 0.10 and 0.27. Add acoustic ceiling tile (Class A NRC≥0.9) and confirm blind-out blackout. Confirm CRC Omni clinical brief for sensory specification. | 40009 rows 0.10 SENSORY ROOM and 0.27 SENSORY ROOM both 'Washable matt emulsion paint, enhanced durability'. | 11606-XX-ZZZ-SH-RHA-AR-40009 | ARCH_DESIGNER | OPEN
A-116 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Stair Layout — Handrails | Drawing 25001 | TGD K 2014 §1.5 — handrail required to both sides where stair ≥1000mm wide; BS 8300-2 §5.9 for accessible stairs (both sides); ergonomic 900/1100mm | Plan shows 'WALL MOUNTED HAND RAIL' on one side only with notes 1100mm and 900mm. Roof-access stair flight width appears ≥1000mm. Single-side handrail is non-compliant unless utility-only classification confirmed. | Add second wall-mounted handrail on opposite side of stair. Specify continuous, 300mm horizontal extension at top/bottom, return to wall, 50mm Ø stainless steel, contrasting LRV to wall (BS 8300-2). | 25001 plan annotations: 'WALL MOUNTED HAND RAIL 1100 900' — single side shown only. | 11606-44-L00-DR-RHA-AR-25001 | ARCH_DESIGNER | OPEN
A-117 | MEDIUM | ARCHITECTURAL | DOCUMENT_HYGIENE | Roof Construction Details | Drawing filename 16060-37-ZZZ-DR-RHA-AR-52001 | Drawing register integrity; CWMF document control | Roof Detail drawing filename begins '16060' not '11606'. Cross-references to this sheet by project number will fail at downloads/automatic search and confuse BCMS register. Suggests cut-and-paste from another project (16060 is a different RHA job) — file content/Specification suitability needs re-validation. Pattern of cross-project reuse already noted on Elec spec. | Re-issue as 11606-37-ZZZ-DR-RHA-AR-52001. Audit content of the sheet to confirm it relates to the Rathbeale roof build-up (160mm insulation to 1:60 fall, 300mm concrete slab, green roof per J41/110 — content does describe this project; safe). Update drawing register entry. | Filename: '16060-37-ZZZ-DR-RHA-AR-52001- Construction Details - Roof.pdf'. All other drawings begin '11606-'. | 16060-37-ZZZ-DR-RHA-AR-52001 | ARCH_DESIGNER | OPEN
A-119 | MEDIUM | ARCHITECTURAL | DOCUMENT_HYGIENE | Changing Room & Shower Room — Laid to Falls | Drawings 53001 + 53002 | BS 8000-4:1989 plumbing on-site practice; HBN 00-09 wet-area drainage; HTM 64 | Both 53001 and 53002 annotate 'Screed laid to falls' and 'Fall' arrows but no fall ratio (1:60–1:80 typical for shower deck). Floor screed/installer left to determine — ponding risk, slip exposure, infection control fail. | Add explicit fall ratio note (e.g. 'Screed laid to falls 1:60 min, 1:80 max towards gully; gully size 100mm Ø with grease trap where required') to both 53001 and 53002. Show high point and gully location dimensionally. | 53001/53002: 'Screed laid to falls' with 'fall' arrows; no ratio cited anywhere on the sheet. | 11606-XX-L00-DR-RHA-AR-53001 + 53002 | ARCH_DESIGNER | OPEN
A-120 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Accessible WC Room Layouts | Drawings 60005/60009/60011/60022/60029/60030 — all Accessible WCs | TGD M 2022 §1.4.3 — Accessible WC min 2200 deep × 1500 wide; BS 8300-2:2018 Table 12; NDA Building for Everyone Vol 5 | All 6 Accessible WCs are scheduled at 5.32–6.03 m² (e.g. 0.05 5.32 m², 0.29 6.03 m²). TGD M 2022 minimum is 2200×1500 = 3.30 m² internal but BS 8300-2 wheelchair-accessible WC with frontal/lateral choice is 2200×2200 = 4.84 m² and Doc M peninsular layout is 2500×2200 = 5.5 m². At 5.32 m² the room is borderline for both frontal and lateral transfer; carer space tight. Recommend audit each plan against BS 8300-2 Fig 18. | Provide a per-room dimensional take-off plan annotating the 1500×1500 frontal transfer zone and 1500×1500 lateral transfer zone clear of fittings, on 60005/60009/60011/60022/60029/60030. Confirm Room 0.05 (smallest at 5.32 m²) achieves BS 8300-2 Fig 18 transfer zones; otherwise enlarge. | 60005: '0.05 ACCESSIBLE WC 5.32 m²'; 60029: '0.29 ACCESSIBLE WC 6.03 m²'. | 11606-XX-L00-DR-RHA-AR-60005..60030 | ARCH_DESIGNER | OPEN
A-121 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Kitchen Layout — Room 0.17 | Drawings 60017 + 57012 | IS EN 16282-1/7; FSC Condition 5; HSE Catering guidelines; HSA workplace risk | Kitchen detail 57012 shows airfryer, oven (OVE015), hob (COO002), kettle, toaster, dispensers — and a 'Fire Counter shutter' but NO deep-fat fryer, NO extract hood detail, NO gas-isolation valve location, NO 'Lock Stop' / fire suppression interlock callout. If the operational brief excludes deep-fat fryer this is acceptable but must be confirmed; otherwise extract hood and Ansul-type suppression are missing. | Confirm with Employer/CRC Omni Operations: (1) is hot oil/fryer used? If yes, add fryer, Class F extinguisher, hood with grease filter and suppression interlock; (2) confirm cooking is electric only (no gas appliances) since no gas isolation shown; (3) cross-coordinate hood extract footprint with M&E ductwork rise to roof; (4) add 'Lock Stop' / emergency stop button at room exit per IS EN 16282-7. | 57012 detail shows 'airfryer', 'kettle', 'toaster', 'COO002 cooker'; 'Fire Counter shutter' over hatch but no extract canopy, no fryer, no fire-suppression bottle. | 11606-73-ZZZ-DR-RHA-AR-57012 + 11606-XX-L00-DR-RHA-AR-60017 | EMPLOYER | OPEN
A-122 | MEDIUM | ARCHITECTURAL | COMPLIANCE | GA Plan — Ceiling Heights | Drawing 70001 RCP | HBN 00-09 §3 ceiling heights ≥2.7m clinical; HSE/CRC therapy guidance — 2.7m min for hoist clearance + IPS | RCP notes '2.7m min in circulation areas; 2.7m min in treatment rooms…' but every room is annotated +2.735 (2735mm). With suspended grid + plenum + diffuser + hoist track + sprinkler, the clear under-hoist-track height in C/P WC drops below 2.4m — too low for safe ceiling-hoist arc transfer of taller patients. | Increase soffit datum in hoist-equipped rooms (0.06 C/P WC and any other room with HOI001) to ≥3000mm slab soffit so under-track clear is ≥2400mm. Confirm via section through C/P WC. Cross-coordinate with Structural for slab thickening at insert plate. | RCP 70001 typical: 'CEL 01 (+2.735)' across all rooms; note '2.7m min in treatment rooms... assisted bathrooms'. | 11606-45-L00-DR-RHA-AR-70001 | ARCH_DESIGNER | OPEN
A-123 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Internal Doors Schedule — All clinical/therapy doors at 800mm clear | Drawing 40001 all rows | TGD M 2022 §1.4 (800mm min internal) — BUT BS 8300-2:2018 Table 2 + HBN 00-09 §5.7 for healthcare prefer 900mm clear effective for wheelchair-plus-attendant throughflow | All 33 doors scheduled at 800mm clear ope. TGD M minimum met but BS 8300-2 / HBN healthcare best practice is 900mm. CRC users include adult wheelchair users with carer — 800mm produces wing-touching on entry, ironmongery damage, and slows operations. | Upgrade all doors serving therapy rooms (0.07/0.08/0.12/0.15/0.20/0.23–0.28), and all doors on the principal user circulation to 900mm clear ope (T1.2 structural ope 1050mm or T2 1100mm with vision panel). Maintain 800mm only on staff/back-of-house doors. | 40001 all rows show 'Clear Ope. 800mm'. | 11606-XX-XXX-SH-RHA-AR-40001 | ARCH_DESIGNER | OPEN
A-124 | MEDIUM | ARCHITECTURAL | OPERATIONAL | Ironmongery Schedule — door closers | Drawing 40010 — All Sets except Set 01/24 | TGD M 2022 §1.4 max opening force ≤30N (0–30°), ≤22.5N (30–60°); BS EN 1154 power-rating; BS 8300-2 closer adjustability | Door elevations 40001 cite '≤30N to 30° / ≤22.5N to 60°' but Ironmongery Schedule 40010 does not call out closer EN 1154 power-rating per door size/mass, nor reduced-force closers for accessible doors. Closer 'as Set X' is non-specific. Risk of installer-selected high-power closers exceeding TGD M force limits on therapy / accessible WC doors. | Add to each Set in 40010: closer make/model with EN 1154 power-rating (e.g. EN3 for 800mm leaf, EN4 for 950mm). For accessible doors specify free-swing/reduced-force closers (e.g. Briton 996 with backcheck) verified to comply with 30N at 30°. | 40010 Sets listed only by Set No. + descriptive function; no closer EN-rating column. | 11606-XX-L00-SH-RHA-AR-40010 | ARCH_DESIGNER | OPEN
A-125 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Internal Doors Schedule — Vision Panel glazing | Drawing 40001 — all FD-rated doors with vision panel | BS EN 1634-1 (fire test); BS EN 12150 (toughened) or Pyrostop / Pyran S (fire-rated glass); TGD M vision panel 500–1500mm AFFL | 40001 type T2 description states 'Vision Panel, refer to door schedule. Fire resistant glazing (integrity and insulation) to match fire door rating where necessary' — but Schedule does not name fire-glazing product, manufacturer, certification or sight-line dimensions. FD60S kitchen door D0.009 requires E120/EI60 vision panel — unspecified. | Add glazing-product column to 40001 specifying: integrity rating (E), insulation (I), proprietary system (Pyrobel/Pyrostop/Promat), glazing bead, intumescent strip. For FD60S kitchen door D0.009 confirm E120/EI60. For non-FD doors confirm safety glass to BS EN 12150 with manifestation. | 40001 type T2 elevation note: 'Vision Panel, refer to door schedule. Fire resistant glazing (integrity and insulation) to match fire door rating where necessary.' Schedule does not list glazing product. | 11606-XX-XXX-SH-RHA-AR-40001 | ARCH_DESIGNER | OPEN
A-126 | MEDIUM | ARCHITECTURAL | COST | FF&E Components — Totals | Drawing 40008 | PW-CF5 ED — FF&E supply-and-install boundary must be clear for BoQ pricing; categorisation 1/2/3 (supplied+fixed / fixed-supplied-separate / supplied+fixed separate to contract) | Room layouts 60001–60032 footnote three categories of FF&E but 40008 totals appear unsorted by category, and HOI001 (hoist) is not annotated with which category — is it Cat 1 (contract supplies + installs), Cat 2 (Employer supplies, contractor installs) or Cat 3 (Employer scope)? Cost-category boundary unclear at tender. | Add category column (1/2/3) to 40008 against every FF&E line, with totals per category. Confirm HOI001 hoist category (typically Cat 2 — Employer supplies adjustable equipment, contractor installs base plate + structural insert + electrical supply). | 60001 footnote: '1 - Items supplied and fixed ¦ 2 - Items fixed as contract and supplied separate ¦ 3 - Items supplied and fixed separate to building contract'. 40008 line HOI001 with no category column. | 11606-XX-ZZZ-SH-RHA-AR-40008 | ARCH_DESIGNER | OPEN
A-127 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Sanitary Schedule — Cleaners Store | Drawing 40006 Room 0.03 | HBN 00-10 part C cleaner's room (sluice/janitorial unit standards); HTM 64 | Cleaners Store 0.03 specifies SIN013 Janitorial unit + SNU012 sink + TAP815. No floor gully shown; no spill containment threshold; no chemical store shelving. As built, cleaner waste water can flow into corridor on overflow. HIQA infection control finding likely. | Add floor gully (100mm Ø) to centre of Cleaners Store 0.03; raise threshold 25mm with cove to floor; specify lockable chemical shelf (HSE HCAI control); add to 60003 plan and 40006 sanitary list. | 40006 Room 0.03 list: SIN013, SNU012, TAP815, TAP894.A, WAS107, BAS900 — no floor gully/drain item. | 11606-XX-ZZZ-SH-RHA-AR-40006 + 11606-XX-L00-DR-RHA-AR-60003 | ARCH_DESIGNER | OPEN
A-129 | MEDIUM | ARCHITECTURAL | COMPLIANCE | Curtain Wall fire-stop coordination | Drawing 20001 Elevations + missing 40003 | TGD B Vol 2 2024 §3.5 cavity barriers + slab-edge fire-stopping at curtain wall; BS 8414 cladding fire test where relevant; FSC Cond 2/3 | Elevations 20001 reference CW-01 and CW-09 curtain wall panels. With single-storey building and parapet at +35.900, slab-edge spandrel detail is critical for parapet/coping fire-stop; not detailed in pack (40003 missing). Risk of FSC compliance failure at fire-stopping commissioning. | Issue slab-edge / parapet fire-stop detail at CW interface as part of corrected 40003 (or 59000 series). Confirm cavity barrier continuity and that any combustible insulation in CW spandrel zone is excluded above 11m / per TGD B 2024 (does not apply <11m but document anyway for FSC sign-off). | 20001 Elevations show CW-01, CW-09 — referenced product/spec/fire detail absent from pack (40003 contains stair only). | 11606-XX-XXX-DR-RHA-AR-20001 | ARCH_DESIGNER | OPEN
A-130 | MEDIUM | ARCHITECTURAL | OPERATIONAL | Room Layout — Therapy Rooms with Access Control external escape | 40001 D0.021/D0.022/D0.023/D0.025/D0.029 | TGD B Vol 2 §1.3 escape route integrity; HIQA safeguarding | Doors D0.021–D0.029 (Therapy 0.23–0.28) notes 'Access control to both sides. No BGU required - escape provided from external door.' Each therapy room has its own external door. In a lone-working or 1-to-1 therapy session with locked entrance, a service user could be unable to exit through the staff-only external door if it is locked from outside or if external is not on egress path. Lone-worker / safeguarding risk. | Confirm with Employer that external therapy-room doors are operable from inside without key/code at all times (single action lever release) and are on a safe external pathway. Add note to schedule cross-referencing emergency override. Confirm fire-alarm release of external door mag-locks if any. | 40001 D0.021/D0.022/D0.023/D0.025/D0.029 Notes: 'Access control to both sides. No BGU required - escape provided from external door.' | 11606-XX-XXX-SH-RHA-AR-40001 | ARCH_DESIGNER | OPEN
E-113 | MEDIUM | ELECTRICAL | DESIGN_INCOMPLETE | Drawing 1743_64(00) Containment | Cable containment / segregation | I.S. 10101:2020+A1:2024 §528; I.S. 3218:2024 §16.2.3 separation of fire cables | Drawing 1743_64(00) shows 'TYPICAL SEGREGATION OF CIRCUITS' with colour-coded compartments for ICT / Fire & Life Safety / Misc ELV / LV Power. Good practice. However: (a) No minimum separation distance stated between LV power and ELV (data, fire, security) — I.S. 10101 §528.1 requires 50mm or barrier, (b) No fire-rated cable trunking specified for fire alarm at penetrations through fire-rated walls/floors (Promat/Hilti firestop required per FSC), (c) Drawing notes 'CONTRACTOR MUST ALLOW FOR FULL CO-ORDINATION OF ALL CONTAINMENT' but no MEP-coordinated containment drawing issued — BIM clash detection not evidenced, (d) Bracket loading: 'UNISTRUT QUICK FIX – PRE GALVANIZED' shown — confirm BCAR design cert per spec §6.00 covers all suspension systems. | Issue updated 1743_64(00) annotation with explicit segregation: 50mm clear separation OR continuous fire-rated barrier between fire alarm cable and LV power. Issue separate Builder's Work / Firestopping Schedule listing every fire-compartment penetration with FRL and approved seal product. Confirm BIM-coordinated containment model has been issued — if not, mark as design-and-coordinate by contractor with risk allowance. | Drawing 1743_64(00) typical segregation legend: 'ICT CABLES / FIRE & LIFE SAFETY / MISC ELV CIRCUITS / LV POWER CABLES'; note 'CONTRACTOR MUST ALLOW FOR FULL CO-ORDINATED CONTAINMENT' but no clash-detection model referenced | 1743_64_00.pdf | EE_DESIGNER | OPEN
E-114 | MEDIUM | ELECTRICAL | DESIGN_INCOMPLETE | Drawing 1743_62(00) + Spec §8.03 | Small power / socket density | CIBSE LG7; HBN 00-09 (planning + design of healthcare environments) | Drawing 1743_62(00) shows socket distribution typical for office building — 4-gang switched at most desks, twin sockets at perimeter. Healthcare day-care needs: (a) higher socket density per room — minimum 2× double-sockets per therapy bed/chair position (HBN 00-09), (b) clean/dirty utility area socket grouping with colour-coded covers (red/green for clean/dirty), (c) RCBO per circuit (not shared) for vulnerable users, (d) USB-C charging at staff base & reception (modern healthcare standard), (e) accessible isolators at 850–1100mm AFFL per TGD-M, (f) IP65 sockets in any wet treatment area, (g) emergency-quality power for clinical-grade equipment if any (oxygen concentrators, suction). Spec §8.03 only states 'switched 13A 3 pin... mounted generally at 400mm AFFL'. Spec note 'Outlets at 150mm above bench level' conflicts with kitchen worktop heights without coordination. | Issue room-by-room small-power schedule listing socket count, type (IP rating), RCBO discrimination (1 RCBO per room minimum, not shared), USB-C provision, accessible isolator height confirmation. For sensory/therapy rooms, ensure circuit segregation so failure of one socket does not lose room. Confirm with end-user (CRC) clinical equipment expected at each position. Add 'all kitchen sockets above worktop to be IP54 minimum'. | Drawing 1743_62(00) sockets indicated by symbol but no per-room loading table; spec §8.03 'Service sockets shall be switched 13A 3 pin with shuttered receivers... Socket outlets shall be mounted generally at 400mm AFFL and 150mm above bench level' | 1743_62_00.pdf; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-115 | MEDIUM | ELECTRICAL | DESIGN_INCOMPLETE | Drawing 1743_68(00) + Spec §12.19 | CCTV system + data privacy | GDPR Art 6 + Art 35 (DPIA); Data Protection Act 2018; HSE Data Protection Policy | Drawing 1743_68(00) shows extensive CCTV including internal cameras (in therapy rooms?? unclear from schematic). Spec §12.19 specifies '16 TB Storage Capacity', 'remote offsite access', 'live monitor and remote access the system'. Issues: (a) no statement of DPIA (Data Protection Impact Assessment) — mandatory for healthcare CCTV per GDPR Art 35, (b) no retention period stated — HSE default is 28–31 days max, (c) no statement of encryption at rest, (d) 'remote offsite access' creates international transfer risk if cloud-hosted outside EEA — must be confirmed, (e) cameras inside therapy rooms would be highly sensitive — confirm with client + Service Users' privacy advocate before specifying internal camera placements, (f) signage at all entrances required by GDPR + access to footage by data subject must be procedural. | (1) Mandatory: HSE Privacy Office DPIA before any internal CCTV. (2) Re-issue drawing 1743_68(00) with EXTERNAL ONLY CCTV unless DPIA approves internal. (3) Spec to state: 28-day retention, AES-256 encryption at rest, EEA-only hosting, GDPR signage at every entrance, documented access procedure. (4) Cross-ref to architect for sign placement. | Drawing 1743_68(00) shows multiple CCTV cameras including positions inside what appear to be therapy/activity rooms; spec §12.19 'System to be complete with facility for remote offsite access to enable client or appointed monitoring company to live monitor and remote access the system'; no DPIA reference, no retention period, no encryption clause. | 1743_68_00.pdf; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-116 | MEDIUM | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Electrical Specification | §12.23 Staff Attack System | BS 8484:2022 Lone Worker; HSE Workplace Violence Policy 2018 | Spec §12.23 specifies 'Staff Attack System' with 10 staff pendants using 'smart Liberty devices' with full integration onto 'Schrack Seconet nurse call system'. However: (a) Schrack Seconet is referenced — not previously mentioned elsewhere in spec, no nurse call system in BoQ Summary (item 62-13 is PA only), no nurse call shown on drawings — undefined scope, (b) BS 8484 lone-worker compliance not stated, (c) panic button location at reception ('SEN base' wording remains from school project — should be 'reception/main staff area'), (d) staff attack alarm must summon assistance — escalation path (to manager/security/external?) not defined, (e) location-tracking pendants raise GDPR Art 35 DPIA questions for staff, (f) 'SEN base' is School Education Needs term — not applicable to CRC day-care. | Confirm with client + CRC clinical lead whether staff-attack/lone-worker is required (likely yes given service user profile). If yes: specify BS 8484-compliant system, defined escalation path, GDPR consultation for location tracking, integration with fire alarm panel for location-aware alerts. Delete 'SEN base' wording. Confirm Schrack Seconet system inclusion or remove integration clauses if not specified. | §12.23 'A Staff Attack System complete with 10 no staff pendants to be provided for the SEN base, the system will comprise of real-time location'; 'The smart Liberty devices shall be fully integrated onto the Schrack Seconet nurse call system' [Schrack Seconet not specified elsewhere] | Electrical Specification .pdf | EE_DESIGNER | OPEN
E-117 | MEDIUM | ELECTRICAL | DESIGN_INCOMPLETE | Electrical Specification | §8.08 Wiring for Lift Installation / §9.0 Standby Generator | Project scope — single storey, no lift, no generator | §8.08 contains a complete lift specification: '32 Amp TP&N power supply', 'lift car lighting', 'lift shaft lighting', 'lift pit', 'IS EN-81-1:1999'. The building is SINGLE-STOREY — no lift required. Risk: contractor (a) prices phantom lift scope creating cost dispute, or (b) ignores section then claims later it should have been removed. Similarly §9.0 'Standby Generator: Not Applicable to this project' is correctly worded but the question of essential supplies for vulnerable users in a power outage remains unanswered. HTM 06-01 Class C minimum (90 minutes ride-through) typically expected at healthcare day-care for: emergency lighting, fire alarm, refrigeration of any medication, BMS, comms, CCTV. UPS for IT comms rack noted on drawing 1743_69(04) but not confirmed sized for full building essential load. | DELETE §8.08 entirely (no lift). Confirm with HSE/CRC whether mini-UPS at meter cabinet (15 min ride-through) or full standby generator (HTM 06-01 Class C) required. If UPS only, size for: fire alarm + emergency lighting (already self-contained) + comms rack + access control + CCTV + medication fridge (if any) — typically 3–5 kVA UPS. Add to BoQ. Provide in spec with battery sizing calculation. | §8.08 'Wiring for Lift Installation: The lift installation shall be fully suited for disabled use in accordance with building regulations part M and IS EN-81-1:1999... 32 Amp TP&N lockable isolator located within the lift shaft adjacent to the lift control panel'; §9.0 'Standby Generator: Not Applicable to this project' | Electrical Specification .pdf | EE_DESIGNER | OPEN
E-118 | MEDIUM | ELECTRICAL | REGULATORY_NONCOMPLIANCE | Electrical Specification | §15.0 Summary of Tender / Final | Revenue VAT rates (Ireland 2026); PW-CF5 §6.2 | Form of Tender at Spec §15.0 includes 'Add V.A.T. ( State VAT Rate ) ...................... %' with two pre-printed lines for 'VAT @ 13.5%' and 'VAT @ 21%'. Ireland standard VAT is 23% (since 2012). Construction services VAT is 13.5%. There is no 21% VAT rate currently in Ireland. This is the same defect flagged in Round 1 — persisting. Tender comparator will be invalid; contractor may price at wrong VAT then dispute. Also Pricing Doc references BoQ items 62-14 'classroom trunking', 62-12 'GP Hall' induction loop — both school scope. | Re-issue Form of Tender with correct Irish VAT rates: 13.5% (construction services), 23% (goods & professional services where applicable). Delete '21%' line. Strip school-scope BoQ items (62-12, 62-14) and replace with day-care scope. Confirm with QS the VAT split for construction vs goods is consistent with PW-CF5 Schedule of Rates. | §15.0 MAIN SUMMARY OF TENDER 'VAT @ 13.5 % / VAT @ 21 %' [21% is not a current Irish VAT rate]; BoQ items '62-12 Induction loop systems in classrooms and GP Hall', '62-14 classroom trunking system' | Electrical Specification .pdf | EE_DESIGNER | OPEN
E-119 | MEDIUM | ELECTRICAL | DESIGN_INCOMPLETE | Drawing 1743_65 BMS Controls 00 + 01 | BMS coverage + interfaces | BSRIA BG 49 (Commissioning); CIBSE Commissioning Code C (BMS); FSC C&E matrix | Drawings 1743_65(00) & (01) show BMS field devices, valves, dampers, thermostats but: (a) No cause-and-effect matrix between BMS, fire alarm, AOV, ventilation, refrigeration. FSC requires C&E to be issued by contractor and witnessed by Fire Engineer at commissioning, (b) No BMS Network Architecture diagram (BACnet/IP, Modbus, Lonworks) — drawing 1743_69(02) shows 'MCC PANEL - WALL MOUNTED IN BOILERHOUSE - IP54 RATED C/W BMS OUTSTATION CONTROL AND OPEN PROTOCOL' but protocol not named, (c) Front-end PC location 'IN OFFICE' but office (R0.27 Manager's Office) is unattended out-of-hours — should be at reception with read-only secondary, (d) Alarm signalling to HSE Estates Helpdesk not specified. | Issue dedicated Cause-and-Effect Matrix as appendix referencing fire alarm, AOV, ventilation, refrigeration, magnetic door release, lift recall (none here). Specify BMS protocol: BACnet/IP preferred. Confirm front-end location and remote monitoring connection to HSE Estates ticketing system. Include BSRIA BG 49 commissioning level. | Drawing 1743_69(02) 'MCC PANEL - WALL MOUNTED IN BOILERHOUSE - IP54 RATED C/W BMS OUTSTATION CONTROL AND OPEN PROTOCOL'; 1743_69(02) 'FRONT END AND PC LOCATED IN OFFICE'; no C&E matrix included; no BMS network architecture diagram | 1743_65_BMS Controls_00.pdf; 1743_65_BMS Controls_01.pdf; 1743_69_02.pdf | EE_DESIGNER | OPEN
F-004 | MEDIUM | FIRE | COMPLIANCE | FSC Condition 5 — Kitchen suppression | Fire Report Condition 5 (p.3) | IS EN 16282-7; FSC Condition 5 | Condition 5 requires deep-fat-fryer suppression interlinked with fire alarm and gas/electrical isolation, plus 'Lock Stop' switch, plus duct cleaning regime, plus heat detection in extract ductwork. Kitchen scope (Room 0.17 Kitchen layout AR-57012) must reflect this — verify Mech and Elec specs and Architectural Kitchen layout integrate the suppression scope and the Lock Stop location. | Cross-check Kitchen layout drawing AR-57012, Mech spec (extract / suppression), Elec spec (Lock Stop / interlock). Issue addendum if any element absent. | Fire Report Condition 5: 'Where deep fat frying equipment is provided in the premises the cooking equipment and associated ductwork shall be protected by a fire suppression system; all of which is to be installed in accordance with IS EN 16282-7...' | 22481-Stage 2C Report p.3 | ME_DESIGNER | OPEN
F-005 | MEDIUM | FIRE | COMPLIANCE | FSC Condition 7 — Green roof | Fire Report Condition 7 (p.4) | BS 8616:2019 (substrate); DCLG UK 2013 (green roof fire performance); Green Roof Code of Best Practice UK 2014 | Condition 7 references UK guidance documents for green roof fire performance. Confirm these are bound into the Arch spec or M&E spec. Note green roof shown on Arch drawing 12003 (PAVING AREAS & GREEN ROOF — C&S sheet) — coordination between Arch waterproofing spec and C&S structural deck loading. | Confirm BS 8616:2019, DCLG UK 2013 and Green Roof Code of Best Practice UK 2014 are explicitly referenced in the green roof spec. Confirm Irish equivalence of UK documents or accept as best-practice references. | Fire Report Condition 7: 'Where green roofs are provided they shall comply with the following: (i) BS 8616:2019 — Specification for performance parameters and test methods green roof substrates, and (ii) Fire Performance of Green Roofs and Walls - DCLG UK: 2013, and (iii) Green Roof Code of Best Practice UK: 2014.' | 22481-Stage 2C Report p.4 | ARCH_DESIGNER | OPEN
F-006 | MEDIUM | FIRE | COMPLIANCE | FSC Condition 2 — Fire detection | Fire Report Condition 2 (p.3) | IS 3218:2024 | Condition 2 requires fire detection and alarm system to comply with IS 3218:2024. Verify Elec spec and fire alarm scope reference IS 3218:2024 explicitly (not IS 3218:2013 or earlier). Cause-and-effect matrix required per IS 3218:2024 §6 — note user project brief flagged absence. | Confirm IS 3218:2024 cited in Elec spec. Confirm cause-and-effect matrix to be issued as part of tender pack or required as tenderer deliverable. | Condition 2: 'The fire detection and alarm system to comply with IS:3218:2024. Reason: To comply with Part B1...' | 22481-Stage 2C Report p.3 | EE_DESIGNER | OPEN
F-008 | MEDIUM | FIRE | DOCUMENT_HYGIENE | Fire Part B Compliance Report | Report age | Currency of design info at tender issue | Fire Report dated 31/03/2026 — same date as the design changes that triggered the revised FSC/DAC requirement. Today is 27/05/2026 (8 weeks later). Confirm no further design changes since report date that the report does not capture. | Reissue Fire Report dated to coincide with tender issue date, confirming no further design changes or capturing any that have occurred since 31/03/2026. | Fire Report p.1: '31/03/2026'. | 22481-Stage 2C Report p.1 | PSDP | OPEN
H-011 | MEDIUM | HEALTHCARE | MEETING_ROOM_ACOUSTIC_CONFIDENTIALITY | 11606-XX-L00-DR-RHA-AR-11001 GA Plan | Meeting & Consultation 0.32 — 22.25 m² | HTM 08-01 Acoustics Table 1 (consulting room DnT,w ≥45 dB); HIQA Standards Theme 1 (Child-Centred) Standard 1.4 — privacy and dignity; GDPR Article 32 (technical confidentiality measures). | Room 0.32 is the parent meeting / MDT case conference / 'difficult conversations' room for CRC — confidentiality is paramount (clinical findings, child protection discussions, disability diagnosis). The GA plan shows the room adjacent to Lobby 01 (0.33), Plant Room (0.31) and an external wall. Adjacency to Plant Room 0.31 is a critical issue — mechanical plant noise breakthrough will compromise both acoustic privacy AND confidentiality (sound transmission outwards). Wall types are not noted on the GA plan for this junction. No acoustic partition specification (e.g. STC ≥50 / Rw ≥48 dB) shown. The room is also adjacent to circulation Hall 01 (0.37) — staff and visitors will overhear sensitive discussions. | ARCH_DESIGNER to (i) specify acoustic partition Rw ≥48 dB to ALL walls of 0.32 including the Plant Room party wall (likely needing twin-stud construction with resilient bars and double 15 mm AcoustiBoard); (ii) acoustic door (Rw 35 dB minimum) with drop-seal; (iii) suspended acoustic ceiling tile Class A (αw ≥0.9) for absorption; (iv) M-Engineer to confirm Plant Room noise breakout < NR 30 in the consultation room; (v) consider relocating room away from Plant 0.31 boundary entirely. | GA Plan 11001: MEETING & CONSULTATION 0.32 (22.25 m²) shares party wall with PLANT 0.31 (17.54 m²). No acoustic partition type called out. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\11000_GA Plans\11606-XX-L00-DR-RHA-AR-11001- GA Plan - Ground Floor.pdf | ARCH_DESIGNER | OPEN
H-012 | MEDIUM | HEALTHCARE | RECEPTION_VISITOR_CONTROL | 11606-XX-L00-DR-RHA-AR-11001 GA Plan + AR-40010 Ironmongery & Access Control | Entrance Foyer 0.34 (66.77 m²) + Manager's Office 0.18 + Staff Office 0.01 | HSE Capital Estates technical guide — reception control in healthcare premises; Children First Act 2015 — visitor management; HIQA Standards Theme 2 (Effective Services) Standard 2.3 — safe access management. | Entrance Foyer 0.34 (66.77 m²) is a large welcoming space — appropriate for CRC. BUT there is no reception desk shown on the GA plan, no manned visitor sign-in position, no line-of-sight from Manager's Office 0.18 OR Staff Office 0.01 to the entrance. Manager's Office 0.18 (15.88 m²) is set back behind Staff Rest 0.19 with no glazed observation onto the foyer. Access Control schedule AR-40010 does NOT show controlled access between Foyer and the clinical corridors (Hall 02 / Hall 01) — anyone entering the Foyer can walk straight into the therapy zone unchallenged. This is a Children First Act and HIQA visitor-management failure. | ARCH_DESIGNER + E to (i) confirm/add reception desk position with line-of-sight to entrance D0.005 — Manager's Office 0.18 could be relocated/extended; (ii) add maglock + access-controlled door between Entrance Foyer 0.34 and Lobby 01 (0.33) / Hall 02 (0.36) — fail-safe open on fire alarm but normally controlled by reception buzzer; (iii) cross-ref with E for video intercom at entrance; (iv) update Access Control schedule. | GA Plan: ENTRANCE FOYER 0.34 (66.77 m²) opens directly to LOBBY 01 (0.33) and HALL 02 (0.36) — no controlled door between foyer and clinical zones. AR-40010 Ironmongery sets list no access control to D0.030, D0.031 (HALL 01) or D0.019 (HALL 02). | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\40000_Schedules\11606-XX-L00-SH-RHA-AR-40010- Ironmongery & Access Control Plan & Schedule.pdf | ARCH_DESIGNER | OPEN
H-013 | MEDIUM | HEALTHCARE | COURTYARD_ENCLOSURE_SAFEGUARDING | 11606-XX-XXX-DR-RHA-AR-20002 + AR-20003 Courtyard Elevations | Courtyard 01, 02, 03 enclosure walls (5400 mm high) with vertical timber slats | HSE Child Safety in Healthcare Premises; HIQA Standards Theme 7 (Use of Resources) — safe outdoor space; National Disability Authority Building for Everyone Vol 5 §6 — accessible outdoor space; ASD-friendly design principles (NDA). | Courtyard elevations AR-20002 show high enclosure (5400 mm) with 'VERTICAL TIMBER SLATS ON 18MM EXTERNAL GRADE PLY' (spec ref H21/110). Concerns: (1) timber slats with horizontal rails may be climbable for older/agile ASD children — risk of fall from height or unsupervised egress; (2) no anti-climb specification; (3) brickwork above with soldier course is fine; (4) thresholds to courtyards should be checked for FLUSH access (universal design) — see W0.044/W0.045 windows full-height adjacent to courtyards but the access door specification is not shown on these elevations; (5) no soft-fall surface under any vestibular play; (6) no shade structure for sun protection. Drainage shown but no surface differentiation for sensory variation (hard/soft/grass). | ARCH_DESIGNER to (i) confirm timber slat spacing ≤100 mm (anti-climb / anti-trap) and provide smooth flush face inside courtyard with no climbable rails; (ii) confirm courtyard door thresholds are flush (≤15 mm upstand per TGD M); (iii) add soft-fall surface zone (impact attenuated rubber tile EN 1177) for any vestibular activity; (iv) add shade canopy or louvre to at least one courtyard; (v) add hard/soft/textural surface differentiation for sensory play (NDA Vol 5); (vi) plant species: non-toxic, non-allergenic, non-thorny (CRC clinical lead to confirm). | AR-20002 Courtyard 1 View 02: '+35.900 T.O. Parapet; +30.500 Ground FFL; VERTICAL TIMBER SLATS ON 18MM EXTERNAL GRADE PLY. H21/110'. Wall height 5400 mm. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\20000_GA Elevations\11606-XX-XXX-DR-RHA-AR-20002- Courtyard 1 & 2 Elevations.pdf | ARCH_DESIGNER | OPEN
H-014 | MEDIUM | HEALTHCARE | SIGNAGE_COGNITIVE_ACCESSIBILITY | 11606-XX-ZZZ-DR-RHA-AR-17001 Signage Ground Floor | Signage scheme — 49 Room ID + 64 Door Plate + 6 Directional | NDA Building for Everyone Vol 5 §7 Signage; BS 8300-2 §10 Signs and information; HIQA Standards Theme 1 (Child-Centred) — accessible information for service users with cognitive/communication needs. | Signage scheme (AR-17001) provides standard text + pictogram signage but does NOT specify a second tier of SYMBOL / PHOTO-based wayfinding for non-verbal children or those with cognitive disability (PECS / Boardmaker / Widgit-style symbol vocabulary). For a CRC paediatric service this is operationally significant — many service users cannot read text. Tactile signage at standard height (1400–1700 mm) may be unreachable for wheelchair users — BS 8300-2 calls for tactile at 1100–1400 mm range. Colour-contrast of signage against wall finish (white emulsion walls per AR-40009) not verified — risk of LRV differential <30 making signs unreadable for low-vision users. | ARCH_DESIGNER to (i) add symbol/photo overlay to all Room Identification signs per Widgit/PCS standard (cross-ref CRC SLT lead); (ii) confirm tactile sign mounting height per BS 8300-2 Fig 40 (1400–1600 mm for standing, 1100–1400 mm if wheelchair-accessed); (iii) demonstrate LRV ≥30 contrast between sign and mounting wall; (iv) add hearing-loop signage at reception/meeting/sensory rooms. | AR-17001 17000_SIGNAGE Type Count: Sign Type H Room Identification ×49; Sign Type G Door Plates ×64. No symbol overlay system noted; mounting heights not stated. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\17000_Signage Plans\11606-XX-ZZZ-DR-RHA-AR-17001- Signage - Ground Floor.pdf | ARCH_DESIGNER | OPEN
H-015 | MEDIUM | HEALTHCARE | DOCUMENTS_GDPR_STORAGE | 11606-XX-L00-DR-RHA-AR-11001 GA Plan | File & Comms 0.02 — 12.13 m² | GDPR Article 32 (security of processing); HSE Records Retention Policy 2016 (paediatric records to age 26 + 6 years); HIQA Standards Theme 8 (Governance, Leadership and Management) — record-keeping. | File & Comms 0.02 (12.13 m²) is the single space for both physical records storage AND comms/IT racking. For a CDNT this is inadequate — paediatric records must be retained until age 26+6 years (potentially 32 years for an infant client), generating large physical archive. Combined comms equipment heat load + paper records is a fire-load risk. Door D0.002 ironmongery Set 04 (no specific access control listed beyond locking). No fire suppression in records area noted (cross-ref with F findings). No environmental controls noted (humidity, temperature) per ISO 11799 for paper archive. | ARCH_DESIGNER + E + EMPLOYER to (i) confirm whether physical records will be held on-site or scanned-to-cloud (recommended); (ii) if on-site, separate comms rack room from paper records storage; (iii) specify access-controlled door (maglock + audit trail per GDPR Art 32); (iv) M-Engineer to add CRAC/comfort cooling, humidity control, fire detection appropriate to records (VESDA recommended); (v) confirm HSE retention policy alignment with EMPLOYER. | GA Plan 11001: FILE & COMMS 0.02 12.13 m². Door D0.002 controlled by Set 04. No separation of comms rack and paper records on layout. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\11000_GA Plans\11606-XX-L00-DR-RHA-AR-11001- GA Plan - Ground Floor.pdf | ARCH_DESIGNER | OPEN
H-016 | MEDIUM | HEALTHCARE | CLINICAL_WASTE_STREAM | 11606-XX-L00-DR-RHA-AR-11001 GA Plan + AR-40008 FF&E | Building-wide — no dedicated clinical waste storage | HTM 07-01 Safe Management of Healthcare Waste; HSE National Healthcare Waste Management Plan; EPA Waste Management (Healthcare Risk Waste) Regulations 2008. | GA Plan shows no dedicated clinical waste hold area (Sanitary segregated from general waste). For a CDNT with adult Changing Places use (incontinence pads, single-use changing materials, occasional clinical waste from health-care interventions) HTM 07-01 requires a separate waste hold with lockable door, washable surfaces, hand-wash basin, ventilation to outside, accessible by waste contractor without entering clinical zones. There is no external bin store shown on the GA plan either. Without this, mixed waste streams will accumulate inappropriately, breaching Waste Management Regulations and HIQA. | ARCH_DESIGNER + EMPLOYER to (i) confirm clinical waste expected volume (likely incontinence-stream rather than infectious-risk); (ii) add external bin store with segregated bays (general / clinical risk / hygiene-stream incontinence / recycling) accessible from the carpark or service road; (iii) internal pre-collection point — a small hold area off Cleaners Store 0.03 with sealed bins; (iv) update FF&E with WAS900 bins for each waste stream and signage. | GA Plan 11001: No room labelled 'Waste Hold' or 'Bin Store'; no external compound shown. FF&E AR-40008 lists generic WASTE bins (BIN028, BIN040 etc) for individual rooms but no segregated stream storage. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\11000_GA Plans\11606-XX-L00-DR-RHA-AR-11001- GA Plan - Ground Floor.pdf | ARCH_DESIGNER | OPEN
H-017 | MEDIUM | HEALTHCARE | PARENT_FAMILY_ZONE_ABSENT | 11606-XX-L00-DR-RHA-AR-11001 GA Plan | Entrance Foyer 0.34 / Dining Hall 0.16 — parent waiting / breastfeeding / sibling zones | CRC operational service model — paediatric CDNT requires parent waiting during therapy sessions, parent-child interaction space, breastfeeding privacy, sibling occupation; HIQA Standards Theme 1 Standard 1.5 (involving families). | GA plan shows a large Entrance Foyer (66.77 m²) but no defined parent waiting area, no breastfeeding/expressing room, no sibling play corner. CRC sessions typically run 30–90 min — parents wait on site. The Dining Hall 0.16 (39.79 m²) may serve as informal waiting but combined use with therapeutic dining is operationally inefficient. Without dedicated parent space, parents wait in the foyer (no privacy, no occupation for siblings, no power outlet for laptops) — poor service-user experience and undermines the family-centred CDNT model. | EMPLOYER to confirm operational model — does CRC require parents to remain on-site during sessions? If yes, ARCH_DESIGNER to (i) designate a portion of foyer as parent waiting zone with comfortable seating, charging outlets, water dispenser, sibling-friendly distraction zone; (ii) confirm one private cubicle (could be relabel Lobby 02 0.38) for breastfeeding/expressing/private parent consultation with clinician; (iii) parent toilet provision (could be 0.05 ACC WC — needs nappy change table — not currently scheduled). | GA Plan 11001: ENTRANCE FOYER 0.34 66.77 m² (no zoning), DINING HALL 0.16 39.79 m², LOBBY 01 0.33 9.97 m², LOBBY 02 0.38 7.54 m². No room labelled 'Parent Waiting' or 'Family Room' or 'Baby Change'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\11000_GA Plans\11606-XX-L00-DR-RHA-AR-11001- GA Plan - Ground Floor.pdf | EMPLOYER | OPEN
H-018 | MEDIUM | HEALTHCARE | HEARING_LOOP_COVERAGE | 11606-XX-L00-DR-RHA-AR-11001 GA Plan + AR-40008 FF&E + Electrical pack | Entrance Foyer 0.34, Meeting & Consultation 0.32, Reception, Sensory rooms | BS 8300-2 §9.3 Induction loop installation; NDA Building for Everyone Vol 5 §6.7; Equality Act / Disability Act 2005 reasonable accommodation; HIQA Standards Theme 1 Standard 1.7 (communication accommodations). | No hearing-loop installation noted in architectural FF&E AR-40008 or in any room layout for the reception desk, meeting/consultation room, or activity rooms. CRC service users include children with hearing impairment (often co-morbid with disability). Parents/grandparents with hearing aids attending meetings will be unable to participate without an induction loop. Cross-ref with E (electrical) — induction loop amplifier and loop antenna are typically electrical scope. The architectural FF&E should call out the requirement (sign 'T' for telecoil at every loop-equipped space). | ARCH + E to confirm induction loop coverage in (i) Reception (within Entrance Foyer 0.34) — fixed counter loop; (ii) Meeting & Consultation 0.32 — room loop; (iii) Group Therapy 0.08 and Activity Rooms 0.15/0.20 — portable loop; (iv) update FF&E AR-40008 and Signage AR-17001 to add 'T' loop signage where installed. | AR-40008 FF&E Components Totals: no entry for induction loop, hearing loop or 'T' signage. AR-17001 Signage: no 'T' (telecoil) sign type noted. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\40000_Schedules\11606-XX-ZZZ-SH-RHA-AR-40008- Architectural FF&E Components - Totals.pdf | ARCH_DESIGNER | OPEN
H-019 | MEDIUM | HEALTHCARE | WINDOW_OPENING_RESTRICTOR | 11606-XX-XXX-SH-RHA-AR-40002 Windows & External Doors | All openable windows in clinical/child-accessible rooms | HSE Child Safety Standard — openable window restriction (max 100 mm open in any direction where child may fall ≥1.0 m); BS 8213-1 §10 (window safety); HBN 03-01 anti-self-harm window restriction (where applicable to behaviour-of-concern users). | Windows schedule AR-40002 is referenced from GA but the restrictor specification has not been verified in this review. CRC children may include those with self-injurious behaviour, ASD elopement risk, or developmental age inconsistent with chronological age. ALL openable windows in spaces accessible to children must have key-controlled or non-overridable restrictors limiting opening to ≤100 mm. The opening windows W0.044, W0.045 facing courtyard (full-height curtain wall vents per AR-20002) need particular attention — if these are openable they MUST be restricted. | ARCH_DESIGNER to demonstrate on Windows Schedule AR-40002 that every openable window pane in child-accessible rooms has: (i) restrictor limiting opening to 100 mm; (ii) restrictor non-defeatable by child (key or tool override only); (iii) bottom of openable pane ≥1100 mm above FFL where possible; (iv) safety glass to BS EN 12600 Class 1B1 within 800 mm of floor. | AR-20002 Courtyard 1 View 02: 'TRIPLE GLAZED POWDER COATED ALUMINIUM WINDOW' shown to courtyard elevations; restrictor spec not noted on elevation drawings. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\20000_GA Elevations\11606-XX-XXX-DR-RHA-AR-20002- Courtyard 1 & 2 Elevations.pdf | ARCH_DESIGNER | OPEN
H-020 | MEDIUM | HEALTHCARE | STAFF_FACILITY_PROVISION | 11606-73-XXX-DR-RHA-AR-57011 Staff Rest + GA Plan | Staff Rest 0.19 (24.14 m²) + Staff Shower 0.04 (9.65 m²) + Staff Office 0.01 (15.91 m²) | HBN 00-10 Welfare Facilities §3 (Staff facilities); Safety, Health and Welfare at Work Act 2005 + General Application Regulations 2007 Part 2 Ch 1; HIQA Standards Theme 6 Standard 6.3 (staff welfare). | Staff Rest 0.19 at 24.14 m² accommodates approximately 6–8 staff seated simultaneously. A full CDNT typically has 12–20 FTE (PT, OT, SLT, psychology, social work, admin, management, support) — the Staff Rest may be undersized for the team if all break together. Single Staff Shower 0.04 (9.65 m² — over-sized for shower but acts as accessible WC + shower — see Sanitary Schedule which shows it as ACC WC + shower combination). Staff Office 0.01 (15.91 m²) — only one office for ALL clinical staff?? CDNT clinicians require write-up space, confidential phone/video consultation booths. The current scheme cannot support a full MDT. | EMPLOYER to confirm FTE numbers and clinical write-up arrangements (hot-desk? home-working hybrid? dedicated desks?). ARCH_DESIGNER to (i) verify Staff Rest capacity against confirmed FTE — possibly extend into Hall area or reallocate Activity Room 0.20 partly; (ii) confirm whether Staff Office 0.01 is for management only and clinical write-up happens in therapy rooms between sessions; (iii) consider phone-booth pod in Staff Office area for confidential calls. | GA Plan 11001: STAFF REST 0.19 24.14 m²; STAFF SHOWER 0.04 9.65 m²; STAFF OFFICE 0.01 15.91 m²; MANAGER'S OFFICE 0.18 15.88 m². Only one staff office for whole MDT. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\50000_Details\11606-73-XXX-DR-RHA-AR-57011- Staff Rest Layout - Room 0.19.pdf | EMPLOYER | OPEN
H-021 | MEDIUM | HEALTHCARE | SCHEDULE_OF_ACCOMMODATION_SIGN_OFF | CWMF Stage 2C deliverables — Schedule of Accommodation | Stage 2C deliverables pack | HSE Capital Works Management Framework Stage 2C — formal SoA sign-off against operational brief; CWMF Stage 2(c) Information Issue requirements. | No formal Schedule of Accommodation (SoA) document discovered in the Stage 2C pack reviewed for this finding set. Without an SoA signed off by the EMPLOYER's operational lead (CRC clinical director) against the room sizes, FF&E, equipment Group 1–4 split, and IT/comms drops, tender risk is high: contractor will price what is drawn, EMPLOYER may receive a building that does not match operational expectations on day one. The Architectural FF&E (AR-40008) is component-totals only — not a room-data-sheet per room confirming operational fit. | EMPLOYER to issue formal SoA document for the pack — table of every room × area × occupancy × FF&E × equipment Group (1 contractor-supplied, 2 contractor-installed-client-supplied, 3 client-supplied client-installed, 4 specialist) × IT/comms drops × M&E demand. CRC clinical lead and HSE Estates technical sign-off required before 10-Jun tender issue. If SoA exists but was not in this reviewed subset, confirm location and circulate. | Stage 2C pack reviewed contains GA Plans, Schedules, Sections, Room Layouts but no document titled 'Schedule of Accommodation' or 'Equipment Schedule Group 1-4'. AR-40008 is 'Architectural FF&E Components - Totals' — building-wide totals only. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\40000_Schedules\11606-XX-ZZZ-SH-RHA-AR-40008- Architectural FF&E Components - Totals.pdf | EMPLOYER | OPEN
H-023 | MEDIUM | HEALTHCARE | FIRE_EVACUATION_NON_AMBULANT_SENSORY | 11606-XX-L00-DR-RHA-AR-11001 GA Plan + Fire Safety Certificate Compliance Report (Appendix E) | Fire evacuation strategy for non-ambulant + sensory-processing users | TGD Part B / Fire Safety in Healthcare Premises; HSE Estates HSF guidance for evacuation of mobility-impaired persons; HIQA Standards Theme 5 Standard 5.2 — environment safe in emergency. | Single-storey building so no refuge needed BUT evacuation distance from far west therapy cluster (0.23-0.28) to nearest final exit is significant — needs to be confirmed against TGD B max travel distance for a healthcare assembly building with non-ambulant users (the standard 18 m direct/45 m total may be reduced where wheelchair occupants are present). Cross-ref with existing Fire findings (F-prefix) but specifically here: (i) is the audible fire alarm tone configurable to be ASD-sensory-friendly (visual + low-tone option)? (ii) Are evacuation chair/ski-pad provisions made for non-ambulant users? (iii) Is the evacuation procedure trained on multi-disability user profile? Pure compliance Fire findings are deduped — this finding is the HEALTHCARE operational overlay. | EMPLOYER + ARCH + Fire Consultant to (i) confirm evacuation procedure briefing for CRC clinical team — every session start must include user-specific PEEPs (Personal Emergency Evacuation Plans); (ii) E-Engineer to specify combined visual+audible alarm with multi-tone option (Vimpex Banshee or equivalent with synchronised flash); (iii) provide evacuation chair/ski pad storage at every Hall (currently no equipment storage shown); (iv) sensory-friendly fire drill protocol documented in operational manual (separate from this design pack but flagged here for handover). | GA Plan 11001: Therapy cluster 0.23-0.28 sits at west end; nearest final exits via Hall 02 (0.36) and external doors. No evacuation equipment store shown. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\11000_GA Plans\11606-XX-L00-DR-RHA-AR-11001- GA Plan - Ground Floor.pdf | EMPLOYER | OPEN
M-002 | MEDIUM | M&E | DOCUMENT_HYGIENE | M&E Drawing Issue Sheets | 'Issued By: RM' (initials only) | SI 9/2014 Reg 9 (designer identification — must be named individual); BCAR Code of Practice | M&E issuer identified by initials 'RM' only — no full name, no chartered designation. BCAR Ancillary Cert requires named individual with chartered status. | Reissue M&E sheets with full name and chartered designation of issuer. | M&E Issue Sheet: 'Issued By: RM' on all 3 sheets. | 1743_Drgissue 2C-Issue Sheet 1/2/3 of 3.pdf | ME_DESIGNER | OPEN
M-003 | MEDIUM | M&E | DOCUMENT_HYGIENE | M&E Drawing Issue Sheets | Circulation list | PW-CF5 appointment register; BCAR participant matrix | M&E circulation lists Client, Architect, QS, Structural Eng, Fire Consultant (TBC), Main Contractor (TBC), Electrical Contractor (TBC), Mechanical Contractor (TBC), Other (N/A). NO Employer's Representative (ER), NO PSDP, NO Assigned Certifier listed. Required PW-CF5 / BCAR roles absent from circulation. | Add ER, PSDP, Assigned Certifier to M&E circulation register. Confirm appointment of each and update circulation accordingly. | M&E Issue Sheet Drawing Circulation: Client, Architect, QSurv, Structural Eng, Fire Consultant, Main Contractor, Electrical Contractor, Mechanical Contractor, Other. | 1743_Drgissue 2C-Issue Sheet 1/2/3 of 3.pdf | ME_DESIGNER | OPEN
M-013 | MEDIUM | MECHANICAL | Ventilation — TGD F / CIBSE B2 | Mechanical Specification.pdf | No Ventilation Schedule — design air-change rates / supply rates / Specific Fan Power / NR levels per room not tabulated | TGD F 2019 (Ventilation) Tables 1 & 2; CIBSE Guide B2 (2016) — Ventilation & ductwork, recommended outdoor air rates; CIBSE TM52/TM59 overheating risk; HBN 00-01 General Design Guidance (non-clinical day-care) | Tenderers cannot select MVHR units, attenuators or fans without designed l/s; price ambiguity; risk of under-ventilation in clinical-adjacent spaces, over-ventilation in others (energy penalty); no audit trail for BCAR Stage 3 commissioning sign-off. | Issue a Ventilation Schedule (room number, function, occupancy, design supply l/s, design extract l/s, ACH, NR, design temp, RH, filtration grade). Add Kitchen 0.17 extract rate per CIBSE B2 (commercial domestic = 30-40 ACH or grease-laden whichever applies). Add overheating risk statement under CIBSE TM52 for south-facing therapy/sensory rooms. | Mech Spec §11.0 sets only generic targets: 'Specific Fan Power – Must be 1.6 w/l or less' and '35dBA maximum noise' and 'provide 100% fresh air requirements'. §11.03 says 'See also Schedule of Heat Recovery Units' — no schedule is present in the spec PDF and no MVHR schedule is bound into the drawings package supplied. No room-by-room l/s or ACH given. No design summer/winter internal temperatures stated. No CIBSE TM52 overheating analysis. No specific extract rate for Kitchen 0.17 (commercial vs domestic), Gym 0.07 (sweat load), Sensory Room 0.11 (controlled environment), Group Therapy 0.08 (potential aerosol risk). | Mechanical Specification.pdf §11.0 Ventilation Services Installation ¦ Mechanical Specification.pdf §11.03 Mechanical Ventilation Heat Recovery Units | ME_DESIGNER | OPEN
M-014 | MEDIUM | MECHANICAL | BMS / Controls | Mechanical Specification.pdf | BMS specification — Points List, Control Strategy Narrative and BSRIA BG 4/2018 commissioning protocol absent | BSRIA BG 4/2018 Whole Building Performance — BMS commissioning; BSRIA BG 9/2011 BMS Engineering manual; BSRIA BG 54/2018 (Soft Landings); CIBSE Guide H Building Control Systems; HSE Estates guidance on BMS networks (security and remote access) | Specialist BMS contractor cannot price; client cannot validate BMS scope; risk of generic 'box-ticking' BMS that delivers poor seasonal performance; HSE Estates remote-monitoring obligation un-addressed; cyber-security gap (NIS2 implications for healthcare). | Issue (a) Full BMS Points List per AHU/MVHR/Heat Pump/UFH zone/CWS booster/expansion/pressure stat/water meter; (b) Cause & Effect / Sequence of Operations narrative per system; (c) BSRIA BG 4/2018 commissioning programme deliverable; (d) graphics schedule (system overviews, plan views, alarms); (e) cyber-security clause (NIS2 / HSE Estates network segregation, MFA, no default credentials). | Mech Spec §12.0 describes hardware (MCC, BACnet controller, touch screen) and §12.19 lists I/O types — but there is NO room-by-room Points List, NO Cause & Effect / Sequence of Operations narrative, NO commissioning plan referencing BSRIA BG 4 or BSRIA BG 9, NO cyber-security requirement (network segregation, default password change, remote access policy), NO graphics deliverable schedule. §12.20 says only 'multiple passwords (minimum of 5)'. The reference to drawings '59, 65, 69 series' for Mech BMS schematic — schematic was not provided in the sampled set. | Mechanical Specification.pdf §12.0 BMS / Automatic Controls ¦ Mechanical Specification.pdf §12.19 BMS Controller ¦ Mechanical Specification.pdf §12.20 BMS Interface Touch Screen | ME_DESIGNER | OPEN
M-015 | MEDIUM | MECHANICAL | Water hygiene / Cold-water storage | Mechanical Specification.pdf | Format 30 break tank exposed at roof level — risk of microbial growth, freeze and tank-to-building thermal bridge | HTM 04-01 Part B §6.7 (Cold water storage); BS 8558 §16 (Cold water storage temperature 5–20 °C and turnover); HSE Ireland Legionella Guidelines 2009; CIBSE Guide G §3 (Public Health Engineering — storage) | Exposed tank in Irish climate: (a) thermal gain on hot summer day risks >20 °C inside tank → Legionella growth; (b) freeze risk in winter on overflow / lid seal; (c) U-value '2.0 W/m²K' is poor insulation by modern standards (should be ≤0.4 W/m²K for cold storage); (d) 4,500 L for ~30-person day-care implies excessive storage and slow turnover. | ME Designer to (1) verify tank size against actual daily demand × 24 h turnover; (2) house tank within a thermally protected and insect-screened enclosure or relocate to insulated tank room; (3) specify shaded location, white finish, or solar-shield cover; (4) add trace-heat / lagging on overflow and warning pipe; (5) confirm U-value of insulation (2.0 W/m²K appears to be a typo — should be much lower); (6) confirm sizing per BS 8558 16.3.2. | Spec §10.07 'A New COLD Water Break Tank to Format 30 Specification is to be installed within exposed at roof level' (sic). 'Tank to the specially insulated from factory to 2.0w/m2k to further prevent possibility of bacteria growth' (sic). 4,500 L capacity for a small day-care centre — likely >24 h turnover. No external weather enclosure noted. No trace heating on tank inlet/overflow. §6.04 trace heating only applies to 'external cold and mains water pipework'. | Mechanical Specification.pdf §10.07 New Cold Water Storage Tank ¦ Mechanical Specification.pdf §6.04 External Water Services pipework | ME_DESIGNER | OPEN
M-016 | MEDIUM | MECHANICAL | Medical Gas (HTM 02-01) | Mechanical Specification.pdf | MGPS / HTM 02-01 — Day-care building may contain therapy/sensory rooms requiring medical gas; not addressed | HTM 02-01 Part A (Design, installation, validation and verification of MGPS); HTM 02-01 Part B (Operational management); I.S. EN ISO 7396-1 (MGPS); HSE Ireland MGPS Code of Practice | If even portable O2 cylinders will be present (likely), spec should reference HTM 02-01 cylinder storage, ventilation of cylinder store (HBN gas storage), and electrical zoning for medical electrical equipment (I.S. EN 60601-1 / IEC 60364-7-710). If MGPS is required, full HTM 02-01 design, AVSU panels, alarm panel and validation regime needed. | ME Designer (via Client/HSE Estates clinical brief) to confirm clinical model — whether centre will store/use portable O2 cylinders, portable suction, or any piped medical gas. If portable only: add cylinder store ventilation + signage + restraint per HTM 02-01 Part B. If piped: add full HTM 02-01 design package. | Mech Spec is silent on MGPS. Building includes Group Therapy Room 0.08 (26 m²), Sensory Room 0.11 (8 m²), Therapy Rooms 0.12, plus Activity Rooms 13 + 15. None are scheduled with O2 / Med Air / Suction terminals on the sampled mechanical drawings, but the HSE day-care typology for adults with intellectual / physical disabilities frequently requires portable suction (CRC service users) and may require emergency O2. | Mechanical Specification.pdf (silent) ¦ Sanitary Schedule + Room Layouts (Therapy/Sensory rooms) | ME_DESIGNER | OPEN
M-017 | MEDIUM | MECHANICAL | Ventilation (HTM 03-01) | Mechanical Specification.pdf | HTM 03-01 specialised ventilation — clinical procedure / treatment rooms not assessed for grade | HTM 03-01 Specialised ventilation for healthcare premises Parts A & B; HBN 12 Out-patients department (vol 4); CIBSE Knowledge Series KS17 Healthcare ventilation | If any clinical procedure (e.g. dental, minor surgical, even immunosuppressed patient consult) is performed, HTM 03-01 air-change rates and pressure regime apply (Grade 'General clinical' minimum 6 ACH supply, F7 filtration, pressure regime defined). Spec does not establish this. | Designer to obtain Clinical Brief and apply HTM 03-01 Table 1 to each treatment / therapy / activity space. Issue revised Ventilation Schedule (linked to finding M-013). | Mech Spec §11 ventilation strategy is decentralised MVHR + extract — no HTM 03-01 grade applied. Group Therapy Room 0.08, Therapy Rooms 0.12, Activity Rooms 13/15 are not categorised. No pressure regime (positive/negative) is stated for any room. Filtration F7 is only on supply at the MVHR unit — adequate for general office but may be inadequate if any minor procedure or treatment is performed. | Mechanical Specification.pdf §11.03 MVHR Units (F7 filter cited) ¦ Sanitary Schedule + Room Layouts | ME_DESIGNER | OPEN
M-018 | MEDIUM | MECHANICAL | Drainage (TGD H + healthcare) | Mechanical Specification.pdf | Drainage — sluice / dirty utility / clinical drainage strategy not addressed (HTM 04-01 / HTM 07-01) | TGD H 2016 (Drainage and Waste Water Disposal); I.S. EN 12056 (Gravity drainage); HTM 07-01 Safe management of healthcare waste; HTM 04-01 Part C (Drainage); BS 8580-2 (Water risk assessment for non-Legionella waterborne pathogens — P. aeruginosa, etc.) | Lack of strategy statement leaves tender risk on clinical waste handling. If incontinence pads or bodily-fluid waste arise (likely in adult day-care for disabilities), the spec should align with HTM 07-01. | Designer + Client to confirm clinical model. Insert HTM 07-01 / HTM 04-01-C references and a Clinical Drainage strategy paragraph in §52. Confirm bedpan washer / macerator not required (and document the reason). Confirm clinical waste sluice route per HTM. | Mech Spec §52 Bill of Quantities references 'Soils & Waste drainage system' and 'HepVO traps'. No HTM 07-01 reference, no HTM 04-01 Part C reference. No drawing in the sampled set shows clinical wash trap with isolating compound or dedicated sluice drain. Cleaners Store 0.03 contains SIN013 sink with bucket grating but no clinical-grade sluice / macerator / bedpan washer is in the sanitary schedule (consistent with day-care typology) — but the strategy is not stated explicitly anywhere. | Mechanical Specification.pdf §52 BoQ Soils & Waste ¦ AR-40006 Sanitary Schedule Room 0.03 SIN013 | ME_DESIGNER | OPEN
M-019 | MEDIUM | MECHANICAL | Spec hygiene / drawing referencing | Mechanical Specification.pdf | Spec internal cross-references broken — '57(00)–57(01)' / '53(00)' / '59(00)' / '65 series' / 'Schedule of Booster Pump Sets' / 'Schedule of Heat Recovery Units' / 'Schedule of Circulation Pumps' all referenced but no Schedules document is bound into the spec PDF | PW-CF5 Clause 2 (Contract documents complete and consistent); BSRIA Soft Landings | Tender package incomplete. Tenderers cannot select equipment without scheduled duties. PW-CF5 requires the Employer-Designed documents to be complete at tender issue. | Bind the missing Schedules into the spec or as a numbered appendix. Confirm 59-series and 65-series schematics are in the Tender Drawings drop; confirm Issue Sheets list them at status T (Tender). M-002 logged at parent level on issuer initials applies here. | §9.01: 'Specific Unit details for LPHW System _ Are Outlined on 56 & 59 series drawings'. §10.06: 'See also Schedule of Booster Pump Sets'. §11.03: 'See also Schedule of Heat Recovery Units'. §9.01: 'Circulation Pumps detailed within Schedule of Circulation Pumps'. None of these schedules are within the 117-page mechanical specification PDF and not all schematic drawings (59, 65 series) were provided in the sampled drawing set. | Mechanical Specification.pdf §9.01 / §10.06 / §11.03 / §11.05 / §11.06 ¦ Drawing Issue Sheet 1-3 of 3 (status confirmation required) | ME_DESIGNER | OPEN
M-020 | MEDIUM | MECHANICAL | Kitchen extract / Fire Resistant Ductwor | Mechanical Specification.pdf | Fire-resistant kitchen extract spec is generic — not aligned with Condition 5 or with absence of deep-fat fryer | FSC Condition 5; I.S. EN 16282-1 to -8; TGD-B 2024 §3.5.25; BS 9999:2017 §32 (Ventilation); HVCA TR/19 (Guide to good practice — internal cleanliness of ventilation systems) | If deep-fat fryer is excluded (per M-006 path A), the fire-resistant ductwork spec is over-spec and over-cost; if included (path B) the spec is grossly under-spec. Either way, current document is internally inconsistent. | Resolve M-006 first, then either (a) remove fire-resistant kitchen-extract section, retain only access doors at 3 m for TR/19 cleaning regime; or (b) expand into a full §11.X Kitchen Extract section per EN 16282 series. | §5.03 'Ductwork: Fire Resistant' specifies Firebar BW11 / BS 476-24 (Method 3 BS 5588-9). No mention of (a) whether kitchen extract serves a commercial-grade range hood, (b) grease management / TR/19 cleaning frequency, (c) fusible-link spec for kitchen extract, (d) shunt-tripping the fire alarm, (e) commissioning of suppression system. §5.10 access-door 'Grease-effected ductwork – 3m centres' is a single nod toward kitchen extract but is orphaned from a cohesive kitchen extract spec. | Mechanical Specification.pdf §5.03 Ductwork: Fire Resistant ¦ Mechanical Specification.pdf §5.10 Access Openings (grease 3m centres) | ME_DESIGNER | OPEN
M-021 | MEDIUM | MECHANICAL | Coordination M&E | Mechanical Specification.pdf | Electrical / mechanical interface for hoist, kitchen Lock Stop, MVHR power and Heat-Pump electrical infrastructure under-coordinated | PW-CF5 Clause 9; HTM 06-01 Electrical services in healthcare premises; I.S. 10101:2020+A1:2024 National Rules for Electrical Installations | Risk of late electrical sub-contractor extras and MDB undersizing. | Produce M&E Interface Schedule (one A3 spreadsheet) covering every cross-discipline interface, signed by both ME Designer and Elec Designer pre-tender. Cross-reference E-side findings. | Mech Spec §3.31 Co-ordination is a generic statement only. No interface schedule exists for: (a) hoist motor 230 V supply + isolator location (M-007); (b) kitchen Lock Stop wiring to gas-solenoid / cooker switch / MCB (M-006); (c) MVHR unit electrical supply per unit (6 units listed in BoQ 57-01 but no electrical demand schedule per unit); (d) heat-pump electrical infrastructure (§9.02 says 32 A circuit, 5G x 6 mm² — but two units = 64 A diversified + DHW heat pump = >100 A — need MDB capacity check with Elec Designer); (e) BMS power supply origin. | Mechanical Specification.pdf §3.31 Co-ordination ¦ Mechanical Specification.pdf §9.02 Heat pump electrical data ¦ Mechanical Specification.pdf §11.03 + BoQ §57-01 MVHR (6 units) | ME_DESIGNER | OPEN
M-022 | MEDIUM | MECHANICAL | Acoustic (HTM 08-01) | Mechanical Specification.pdf | Acoustic — NR criteria too coarse for healthcare therapy/sensory environment; HTM 08-01 acoustics not applied | HTM 08-01 Acoustics; HBN 00-01 §6 Acoustic design; BB93 (UK educational reference); BS 8233:2014 Sound insulation; CIBSE Guide A §1.7 (acoustic comfort) | Sensory rooms require near-silent ventilation; un-attenuated MVHR boost mode will be intrusive. Therapy rooms need NR 30 max for speech intelligibility. Generic NR 35 is inadequate for purpose. | Apply HTM 08-01 / HBN 00-01 acoustic table per room type. Reissue acoustic criteria with RT (s) and Lnight criterion for sensory. Re-select attenuators downstream of MVHR units. | Mech Spec §15.02: 'Plant Rooms NR 60, Toilets NR 35, Kitchen NR 35, Public Areas NR 35'. No criterion for Sensory Room 0.11 (typically NR 25–30 for low-stimulus environment), Therapy Room 0.12 (NR 30 for speech privacy), Group Therapy 0.08, Activity Rooms, or Quiet Room. No reverberation time (RT) criterion. No reference to HTM 08-01 or BB93. | Mechanical Specification.pdf §15.02 Noise Criteria ¦ Room Layouts (Sensory 0.11, Therapy 0.12) | ME_DESIGNER | OPEN
M-023 | MEDIUM | MECHANICAL | Commissioning | Mechanical Specification.pdf | Commissioning regime cites CIBSE Codes A/B/C/W only — BSRIA BG 4/2018, BG 49 (Domestic Hot Water), BG 50 (Fire Damper), BG 6/2018 (Pre-commissioning Cleaning) not referenced | BSRIA BG 4/2018 Building Performance Tracking; BG 6/2018 Pre-commissioning Cleaning; BG 49/2015 Commissioning Hot Water Systems; BG 50/2013 Fire Damper Commissioning; PW-CF5 Schedule (commissioning) | Sub-contractor may interpret commissioning scope narrowly. Pre-commissioning cleaning (critical for heat-pump system to avoid plate-HX fouling) un-quantified. Fire damper drop-test regime un-specified. Hot-water Legionella commissioning regime un-specified. | Add BSRIA BG 4/2018, BG 6/2018, BG 49, BG 50 to §14.02. Add explicit drop-test programme for fire dampers (annual + handover). Add 28-day occupancy commissioning return visit per BSRIA Soft Landings BG 54/2018. | Mech Spec §14.02 Standards lists 'CIBSE Commissioning Codes A/B/C/W' and 'DW/143' only. No BSRIA references. §3.41 Manuals references 'BSRIA application guide 1187.1' — but that is a single reference and BG 1187 series is the O&M format guide, not the commissioning protocol. | Mechanical Specification.pdf §14.02 Standards and Conditions ¦ Mechanical Specification.pdf §3.41 Manuals | ME_DESIGNER | OPEN
M-109 | MEDIUM | MECHANICAL | PLUMBING_BACKFLOW | Drg 1743_53_00 | Backflow prevention — Cat 3 / Cat 5 fluids | IS EN 1717, BS 8558 §6, Irish Water Code of Practice §G, HTM 04-01 | No backflow prevention devices are scheduled for cleaner sink (Cat 5), dishwasher (Cat 3), garden tap (Cat 4/5), or boiler/heating fill loop (Cat 4) on Drg 53_00. Heating fill line description in §9.06 mentions only 'isolation valves, check valve, non-return valve and flexible connection' — IS EN 1717 requires RPZ (BA-type) or AA/AB air-gap for category 4 heating systems with chemical dosing. Risk of contamination of incoming potable main and Irish Water non-compliance notice. | Schedule backflow devices by category per IS EN 1717: cleaner sink AB air gap; dishwasher AA/AG or HC; heating fill RPZ BA-type with test ports; garden tap double check DC; reflect on Drg 53_00 and add to BoQ 53-04. | Drg 53_00 distribution shows isolation valves only; Mech Spec §9.06 'fill line will comprise of isolation valves, check valve, non-return valve and flexible connection' — does not meet IS EN 1717 Cat 4 for heating fill. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_53_00.pdf | ME_DESIGNER | OPEN
M-111 | MEDIUM | MECHANICAL | HEATING_BUFFER | Drg 1743_56_00 + Spec §9.01 | LPHW buffer vessel sizing | CIBSE AM16 / BSRIA BG 16 (heat-pump system design); MCS Heat Pump Guide; manufacturer minimum-volume requirements | Spec §9.01 lists '400L stainless steel buffer vessel c/w 2x 6kW immersions'. For 2 × 22 kW = 44 kW total heat-pump output, MCS heat-pump sizing rule of thumb is 10-25 L/kW = 440-1,100 L. 400 L is below the lower bound and risks short-cycling the compressors, loss of warranty, and reduced SCOP below the 4.45 spec'd. Also 2 × 6 kW immersions (12 kW) provide insufficient electric backup if either heat pump fails (44-12 = 32 kW shortfall on coldest design day -3°C). | Re-size buffer vessel per heat-pump manufacturer (Mitsubishi) minimum-volume requirement at min capacity, typically 660-880 L for this duty. Document COP-vs-buffer-volume in design submission. Review immersion-backup capacity vs heating design load. | Spec §9.01: '400 Litre Indoor buffer vessel c/w 2x 6kw immersions'; total heat-pump duty 2 × 22 kW. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Specifications\Mechanical Specification.pdf | ME_DESIGNER | OPEN
M-114 | MEDIUM | MECHANICAL | BMS_CONTROLS | Drg 1743_55_00 + Spec §12 | BMS controls narrative | CIBSE Guide H (controls); BSRIA BG 9 (BMS in healthcare); TGD L 2022 §1.4 (energy-controls) | Spec §12.01 lists BMS functions (time, temp, energy optimisation, run/trip, duty-standby, water meter) but no written controls narrative is provided describing: (i) heat-pump COP optimisation strategy (weather compensation curve, return-temp reset); (ii) underfloor zoning logic with manifold motorised-valve control sequencing; (iii) MVHR demand control with humidity / CO2 / PIR sensor inputs; (iv) DHW pasteurisation cycle (re M-106); (v) holiday / setback / occupancy override; (vi) alarm escalation and remote monitoring (mandatory for unmanned HSE day-care). Tenderers cannot price BMS specialist scope correctly. | Issue written 'BMS Controls Narrative & Points Schedule' as supplementary document referenced in tender. Include cause-and-effect for fire, kitchen, plant alarms; weather-compensation curve for heat pump; weekly Legionella pasteurisation cycle; occupancy schedules per HSE day-care opening hours. | Mech Spec §12 'BMS Outstation(s) shall be incorporated within the MCC for the purposes of - Time Control, Temperature Control, Energy Optimization' — no controls narrative or points schedule. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Specifications\Mechanical Specification.pdf | ME_DESIGNER | OPEN
M-115 | MEDIUM | MECHANICAL | COMMISSIONING | Mech Spec §14 | Commissioning standards — BSRIA BG 49 / Soft Landings | CIBSE Commissioning Codes A/B/C/W (already cited); BSRIA BG 49 (Mechanical Commissioning); BSRIA Soft Landings BG 54; GSL Government Soft Landings (HSE Capital Projects requirement) | Spec §14 references CIBSE Commissioning Codes A, B, C, W but omits: (i) BSRIA BG 49 — current best-practice mechanical commissioning framework; (ii) Soft Landings / GSL post-occupancy aftercare regime (mandatory on HSE capital projects); (iii) seasonal commissioning (heat pump must be witnessed in both heating and cooling seasons); (iv) acoustic commissioning verification per Mech Spec §15; (v) BMS witness/sign-off matrix. For a day-care that opens with vulnerable users, undocumented seasonal performance is a clinical comfort and energy bill risk. | Update Spec §14 to require BSRIA BG 49, BSRIA Soft Landings BG 54 with named Soft Landings Champion, seasonal commissioning at +3 months / +9 months post-handover, acoustic witnessing per Mech Spec §15, BMS sign-off matrix prior to PC. | Mech Spec §14.02 lists 'CIBSE Commissioning Codes A, B, C, W' only — no BSRIA BG 49, no Soft Landings, no seasonal recommissioning requirement. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Specifications\Mechanical Specification.pdf | ME_DESIGNER | OPEN
M-116 | MEDIUM | MECHANICAL | DRAINAGE_STACK | Drg 1743_52_00 | Soil stack ventilation / AAV strategy | IS EN 12056-2 (gravity drainage), TGD-H §1.1.6, BS EN 12380 (Air admittance valves) | Drg 52_00 'BLACK STACK' detail box references 'STUB STACK COMPLETE WITH AIR ADMITTANCE VALVE COMPLYING WITH I.S. EN 12380 TO BE INSTALLED IN ALL STACKS TERMINATED AT HIGH LEVEL... IN COMPLIANCE WITH BUILDING REGULATION H.' For a single-storey day-care with several WC clusters separated across the plan, at least one stack should be fully vented through roof rather than all on AAVs (TGD-H requires at least one open vent per drainage system to maintain main drain ventilation). All-AAV strategy risks foul-air build-up in below-ground drains and possible siphonage of trap seals during peak use (lunchtime). | Confirm at least one stack vented through-roof (typically the longest run / most distant from manhole) per IS EN 12056-2 §6.5. Annotate on Drg 52_00 + 52_01. Confirm AAV access for maintenance in concealed locations. | Drg 52_00 detail box 'STUB STACK COMPLETE WITH AIR ADMITTANCE VALVES COMPLYING WITH I.S. EN 12380 TO BE INSTALLED IN ALL STACKS'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_52_00.pdf | ME_DESIGNER | OPEN
M-117 | MEDIUM | MECHANICAL | CONDENSATE | Drg 1743_52_01 + 1743_57_00 | MVHR condensate drainage from roof-mounted units | CIBSE Guide B2 §3 (condensate drainage); BS 5970 (insulation of condensate pipework); manufacturer requirements | Drg 52_01 shows '40mm CONDENSATE FROM MVHR TO DISCHARGE TO SUITABLE LOCAL DRAIN/GULLY' for each of MVHR 1-6, plus '40mm CONDENSATE FROM HEAT PUMPS'. However the actual route from roof units down to ground gully is not drawn, no trace-heating on external condensate run is specified (Swords frost design ≤-3°C will freeze unprotected condensate), no condensate trap seal detail, and no tundish at discharge to gully. Risk of frost-locked MVHR units, water damage to ceilings if condensate backs up internally, and Legionella risk if external condensate pools into discharge gully. | Add condensate route on roof + downpipe drawing showing trap, fall, trace-heating, insulation (BS 5970), tundish at discharge. Specify electrical heat-trace tape protected to IP66. Update Spec §11 + §53 accordingly. | Drg 52_01: '40mm CONDENSATE FROM MVHR TO DISCHARGE TO SUITABLE LOCAL DRAIN/GULLY' x6 — no route, no trace heating, no trap detail. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_52_01.pdf | ME_DESIGNER | OPEN
M-118 | MEDIUM | MECHANICAL | ACOUSTIC | Mech Spec §15 + Drg 1743_57_00 | Acoustic criteria — therapy rooms vs spec global figure | BB 93 (where applicable for paediatric education spaces), HTM 08-01 (acoustics in healthcare), CIBSE Guide A Table 1.5, NHS HBN 26 | Mech Spec §11.07 sets global ventilation grille noise to 'NR35' but for therapy rooms (CRC clients are largely communication-impaired) the appropriate target is NR25-30. Snoezelen / sensory rooms require near-silent conditions (NR20-25). Spec §15.03 (plant item noise table at perimeter ≤45 dB LAeq) addresses external only. Without per-room NR target, attenuator selection in MVHR ducts (Drg 57_01) will be undersized. Recall noise levels on these CRC sites have triggered planning condition complaints in past — Fingal area is residential. | Issue acoustic room-by-room NR schedule per HTM 08-01: therapy NR30, sensory NR25, dining NR35, offices NR35, kitchen NR40, WC NR35. Re-select attenuators on Drg 57_01 accordingly. Confirm external noise at site boundary ≤45 dB LAeq with heat-pump silent-mode 2 (69 dBA) per Spec §9.02 modelled. | Mech Spec §11.07: 'Sound level NR35' (global, single figure) — does not differentiate sensory / therapy / dining / office. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Specifications\Mechanical Specification.pdf | ME_DESIGNER | OPEN
M-119 | MEDIUM | MECHANICAL | ENERGY_NZEB | Mech Spec §9 + Drg 1743_56_00 | NZEB / Part L 2022 — renewable energy contribution evidence | TGD L 2022 (Buildings other than dwellings, NZEB), SEAI NEAP calculation requirement | Spec §9 establishes SCOP=4.45 for LPHW heat pump and SCOP=3.6 for DHW heat pump, with PV referenced on Drg 50_00 ('PV PV PV PV PV PV...' on roof). However no NEAP calculation, no BER 'A-class' demonstration, no PV array sizing/output (kWp), no calculation reconciling heat-pump renewable energy share with the 20% RES requirement of TGD L 2022 §1.3. Risk of failure to satisfy BC(A)R PartL submission at completion, requiring retrofitted PV or other measures. | Issue NEAP calculation report demonstrating TGD L 2022 NZEB compliance: total energy consumption, primary-energy, CO2 emissions, and RES %. Include PV array schedule (kWp, panel count, inverter, monitoring). Confirm A2 or A1 BER target stated in HSE brief. | Drg 50_00 shows 'PV PV PV PV PV PV' array on south roof but no PV schedule on Drg 56_00 or NEAP report in pack; Mech Spec §9.02 SCOP=4.45. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Drawings\1743_50_00.pdf | ME_DESIGNER | OPEN
M-122 | MEDIUM | MECHANICAL | DUCTWORK_HYGIENE | Mech Spec §5.02.9 | Ductwork hygiene classification — healthcare | BSRIA BG 49 §5; HTM 03-01 (specialised ventilation in healthcare); HVCA TM/1 (ductwork access); SFG 20 | Mech Spec §5.02.9 selects 'Intermediate' ductwork access classification ('Hospitals, Residential Care Premises, Computer Rooms') — appropriate. However spec does not require: (i) BESA TR/19 cleaning regime; (ii) certification of installed ductwork to 'Healthcare' standard hygiene before commissioning; (iii) commissioning air-sampling for ventilation systems serving therapy / sensory rooms (vulnerable users); (iv) HEPA filtration where relevant. Risk of contaminated ductwork at handover, leading to immediate cleaning cost or operational illness risk. | Update Spec §5.02.9 to require BESA TR/19 verification, certified clean-handover, pre-commissioning air-sampling per HTM 03-01 Part B, and post-installation duct inspection with photographic record in O&M. | Mech Spec §5.02.9: 'Intermediate: Hospitals, Residential Care Premises, Computer Rooms' — sets access classification but no cleaning regime or healthcare verification. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Specifications\Mechanical Specification.pdf | ME_DESIGNER | OPEN
S-004 | MEDIUM | C&S | DOCUMENT_HYGIENE | C&S Drawing Register (DR01) | Drawing 00006 'Fire Tender Tracking' | Discipline scope allocation | Fire tender tracking is a fire engineer / TGD-B consultant deliverable, not a C&S deliverable. Either misallocated to C&S or misnamed. Coordination risk between C&S contractor and fire consultant for site logistics. | Confirm correct discipline ownership of drawing 00006. If site logistics for fire appliance access, retain in C&S as access road / fire tender route. If TGD-B B5 fire appliance route compliance, transfer to fire consultant pack and confirm coordination with C&S external works. | DR01: '00006 — FIRE TENDER TRACKING — 08/05/26 — Stefano Duarte / Jim Mansfield'. | DR01 - DRAWINGS REGISTER.pdf | CS_DESIGNER | OPEN
S-005 | MEDIUM | C&S | DOCUMENT_HYGIENE | C&S Drawing Register (DR01) | Drawing number sequence 50001-50009 | Register completeness | Sequence shows 50001, 50002, 50003, 50004, 50005, 50007, 50008, 50009 — drawing 50006 absent. Confirm if intentional omission, withdrawn drawing, or missing from issue. | If 50006 was withdrawn, note in register. If omitted, issue. If never existed, close the gap by renumbering subsequent drawings. | DR01: Sequence 50005 → 50007 with no 50006 entry. | DR01 - DRAWINGS REGISTER.pdf | CS_DESIGNER | OPEN
S-016 | MEDIUM | C&S | QA | Bending_Schedule.xlsx | Header rows 1-5; bar mark 1 | I.S. EN ISO 3766 (Construction drawings — simplified representation of concrete reinforcement); BS 8666:2020 (Scheduling, dimensioning, bending and cutting of steel reinforcement — referenced by Spec clause E.3); BCAR Inspection Plan (bending schedule is the basis for steelfixer inspection). | Bending schedule header lacks: Revision (blank), Drawing Number (blank), Scale (blank), Approved By (blank). Date shown is 30.03.2026 — drifts from drawing-pack date 08.05.2026 and tender date 10.06.2026. Bar mark 1: 321 No. H16 length 6000mm 'TO TRIM ON SITE' shape code 0 — site trimming of high-yield bars without controlled-bend re-bending is forbidden under spec clause E.3.x (no shop-controlled bending = no shape code). Total weight column unverified (no sum line). The schedule is not anchored to any drawing reference so steelfixer cannot trace bars back to elements. | Re-issue bending schedule with: complete metadata block (Drawing No., Rev, Approver, current date); cross-reference column added to every bar mark linking to source drawing and element; bar mark 1 either re-detailed at engineering office with proper shape code or change instruction to 'cut on site to detailer's dimension' with cutting tolerance; total weight summary row; comply fully with EN ISO 3766 shape-code library (BS 8666 superseded by EN ISO 3766 in Ireland). | Header: 'Drawing Number [blank], Revision [blank], Approved By [blank], Date 30.03.2026'. Bar mark 1: '(1, 16, 32, 0, 6000, TO TRIM ON SITE, ...)'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Bending_Schedule.xlsx | CS_DESIGNER | OPEN
S-017 | MEDIUM | C&S | COMPLIANCE | All structural drawings (titleblock dates) vs Drawings Register (sheet issue date) | Titleblock 'Date 16/07/25' vs DR01 'Sheet Issue Date 08/05/26' | BCAR SI 9/2014 Code of Practice (drawings must be unambiguously dated and trackable); ISO 19650 (asset information management). | Every C&S drawing titleblock carries Date '16/07/25' (16-Jul-2025) yet the Drawings Register lists 'Sheet Issue Date 08/05/26' for every sheet. This is a ~10 month discrepancy that suggests the titleblock template was never updated to the current revision date. PDF metadata for spec is CreationDate 22-Apr-2026. Status 'Sheet Issue Date' on register also doesn't show revision letters/numbers. Cross-discipline (C-002) already raised the pack-wide date drift but this register/drawing discrepancy is itself a finding. | Update all C&S drawing titleblocks to current revision and issue date matching the register; introduce a controlled revision table (Rev ¦ Date ¦ Description ¦ By ¦ Chk ¦ Apvd) on every sheet; align register columns 'Current Revision', 'Current Revision Date', 'Current Revision Description' which are currently empty for all 28 sheets. | Drawing 11001 titleblock: 'Date 16/07/25' — Drawings Register row 11001: 'Sheet Issue Date 08/05/26'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\11001 - FOUNDATION PLAN.pdf | CS_DESIGNER | OPEN
S-018 | MEDIUM | C&S | QA | File-naming on disk for RC Sheets RC0002 - RC0007 | Filenames vs Register entries | BCAR document control; ISO 19650 file naming convention; PW-CF5 tender documentation requirements. | On disk, all RC sheets RC0002-RC0007 are saved with the prefix 'RC0001 - RC SHEET 0X.pdf' (i.e. seven files all starting 'RC0001 -'). The Drawings Register correctly lists RC0001 through RC0007 as distinct sheet numbers. A tenderer downloading the pack will see seven 'RC0001-' files and cannot reliably correlate them with the register. Filename and sheet-number must match for QA traceability and Soft Landing checklist. | Re-export and re-zip the C&S tender pack with corrected filenames: 'RC0002 - RC SHEET 02.pdf', 'RC0003 - RC SHEET 03.pdf', ... 'RC0007 - RC SHEET 07.pdf'. Verify ISO 19650 naming convention (Project-Originator-Volume-Level-Type-Role-Number). | Directory listing: 'RC0001 - RC SHEET 01.pdf' through 'RC0001 - RC SHEET 07.pdf' (all seven files start with RC0001). | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\ | CS_DESIGNER | OPEN
S-019 | MEDIUM | C&S | COMPLIANCE | Specification Section E (E.3.x reinforcement clause) | E.3.5 (clause referencing BS 8666) | I.S. EN ISO 3766:2003 (current standard for reinforcement scheduling in Ireland — supersedes BS 8666 in Irish/EU normative context for drawing representation); I.S. EN 10080 (Steel for the reinforcement of concrete — weldable reinforcing steel). | Spec clause E refers to BS 8666 for bar bending. BS 8666 remains a working scheduling standard in UK practice, but for an Irish public-works contract the bending schedule must comply with I.S. EN ISO 3766 (representation) coupled with the bar standard I.S. EN 10080 / I.S. EN 10025 grades. Spec is not wrong, but is now dated (clause dated 28.8.18 footer visible) and risks leaving the contractor to default to UK-only conventions which may not align with the Irish certified rebar supply chain. | Update Section E to reference I.S. EN ISO 3766 as the primary scheduling representation standard with BS 8666 (or its current ISO equivalent ISO 3766) as the dimensioning convention. Reconfirm CARES or equivalent third-party certification chain for rebar supply. | Spec clause E.3.x: 'in accordance with BS 8666 (all subject to sub-section E.3.1 above).' Footer: '28.8.18' across Section E pages. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SPECIFICATION\Specifications - Rathbeale Rd.pdf | CS_DESIGNER | OPEN
S-021 | MEDIUM | C&S | COORDINATION | 11002 - GROUND FLOOR PLAN.pdf | Typical Section through Slab; '78 No. Sheet Mesh A939 for floor slab' | I.S. EN 10080 (mesh designation); I.S. EN 1992-1-1 (slab on grade); BCAR drawing accuracy. | Floor slab annotation reads '78 No. Sheet Mesh A939 for floor slab'. 'A939' is not a standard mesh designation in Ireland (standard meshes are A98, A142, A193, A252, A393, A636, A788). Typographical error for A393. The typical section shows 'A142 Steel fabric reinforcement (400 laps)' — INCONSISTENT with the '78 No. A939/A393' note. Contractor will procure to one of two different mesh weights, creating non-compliance and re-work. Also, '1200 Gauge Visqueen' DPM is dated terminology — modern spec is 'DPM to BS 8102 Type A / IS EN 13967'. | (a) Correct mesh designation to A393 (or whatever is actually intended) and align typ. section with plan note. (b) State whether mesh is one layer top, one layer bottom, or one layer at mid-depth, and what cover. (c) Add radon barrier reference if site is in radon high-risk zone (Swords / Fingal — check radon map; Fingal contains amber/red zones). (d) Modernise membrane spec citation. | Legend on 11002: '78 No. Sheet Mesh A939 for floor slab' alongside typical section text 'A142 Steel fabric reinforcement (400 laps)'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\11002 - GROUND FLOOR PLAN.pdf | CS_DESIGNER | OPEN
S-022 | MEDIUM | C&S | COMPLIANCE | Specification Section A.2 / A.3 + Drawings Register DR01 | Designer/approver columns | BCAR SI 9/2014 Part IIA + Code of Practice for Inspecting and Certifying Buildings and Works (every structural element must have a named Ancillary Cert designer). | Spec A.2 names 'Kavanagh Mansfield & Partners' as the engineer but the Drawings Register shows 'Designed By: Stefano Duarte / Approved By: Jim Mansfield' for ALL sheets, with no allocation of design responsibility for proprietary or sub-contractor-designed items (Isokorb thermal breaks, IG masonry support, green-roof build-up, PV mounting system, hydrobrake flow control, retaining-wall geosynthetics, temporary works). BCAR Ancillary Cert matrix is missing. | Produce a BCAR Ancillary Designer/Builder Cert allocation matrix listing every structural sub-system, the responsible specialist designer (named individual + company), the date of their Ancillary Cert and the file reference. Issue as a new sheet in the C&S pack (00007 BCAR Designer Allocation) or in a section AA of the spec. | DR01 lists 'Designed By: Stefano Duarte / Approved By: Jim Mansfield' for every one of the 28 sheets, with no proprietary/specialist allocation column. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\DR01 - DRAWINGS REGISTER.pdf | CS_DESIGNER | OPEN
S-023 | MEDIUM | C&S | STRUCTURAL_SAFETY | 50005 - RC Walls (Typical).pdf | Wall types A-H sections; 250 RC Wall Section (Typical) | I.S. EN 1992-1-1 + NA (RC wall design); EN 1992-1-1 cl. 9.6 (vertical/horizontal reinforcement minimums in walls); BCAR. | RC Wall sheet shows eight different wall types (A-H) of 250/600/800 mm thickness with reinforcement designation H16-14, H16-15, H10-16/17/18/20/21/22 etc. but: (a) no concrete strength class on the sheet; (b) no cover dimension other than '50mm bottom cover' on the starter-bar detail; (c) no horizontal reinforcement spacing for the 250 mm typical wall (only 'AM393 mesh' shown on the elevation — does this also cover walls 600 mm and 800 mm thick? Almost certainly not — heavy walls need bar-on-bar reinforcement, not mesh); (d) the wall types have no labelled location on the key plan; (e) lap lengths not specified. Risk: under-reinforcement of heavy walls; ambiguity on contractor's BOQ. | Add a 'RC Wall General Notes' panel: concrete grade (e.g. C32/40), cover (e.g. 35 mm nominal both faces), lap lengths in mm by bar size, minimum vertical/horizontal reinforcement ratios per EN 1992 cl. 9.6, link/U-bar arrangement at vertical edges. Add a Wall Type Key plan showing which TYPE applies where. Confirm whether the 'TYPICAL 250 RC WALL' section reinforcement applies also to the 600 mm and 800 mm walls or whether separate sections are required (they are). | Wall types annotated 'H16 -14, H16 -15, H10 -16, H10 -17, H10 -18, H10 -20, H10 -21, H10 -22' with no concrete grade and no cover on the sheet other than '50mm bottom cover' at starter bars. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50005 - RC Walls (Typical).pdf | CS_DESIGNER | OPEN
S-024 | MEDIUM | C&S | COMPLIANCE | Specification Section C, Section SD; Spec footers dated 9.1.20 / 28.8.18 / 18.12.18 | Standard footer of every spec section | PW-CF5 documentation must be current at tender; BCAR Code of Practice (specification current at tender date). | Specification is a KMP boilerplate with sections dated 18.12.18, 9.1.20, 28.8.18. PDF CreationDate is 22-Apr-2026 (re-print of old text). The specification has not been refreshed since 2018-2020 and therefore predates: (a) I.S. EN 206:2013+A2:2021 (current concrete standard amendment), (b) revised CIRIA C753 SuDS Manual 2024 supplement, (c) OPW climate-change uplift guidance 2022, (d) the current Irish NA editions of EN 1990/1991/1992/1993/1996/1997. While the cited core standards remain valid, the spec is not audit-current. | Issue a spec revision certificate confirming the spec text has been verified against current published standards as of 27-May-2026, listing any superseded references that are still acceptable for the contract and any that require updating. Update section footers to reflect re-verification date. | Section A footer '18.12.18' (8 Dec 2018); Section C footer '9.1.20' (9 Jan 2020); Section E footer '28.8.18' (28 Aug 2018). PDF metadata CreationDate '22 April 2026'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SPECIFICATION\Specifications - Rathbeale Rd.pdf | CS_DESIGNER | OPEN
S-026 | MEDIUM | C&S | COORDINATION | 11002 GF Plan (slab spec) + Arch radon zone + Fire compartmentation | Typ. slab section: '1200 Gauge Visqueen grade A (or DPM/Gas barrier to Arch's Details)' | I.S. EN 13967 (DPMs); TGD C (Site preparation — radon); Radiological Protection Institute of Ireland (RPII) radon map for Fingal/Swords; BCAR. | Slab note hedges 'DPM OR Gas barrier to Arch's Details'. Swords sits in an area that may be radon-high (>200 Bq/m³ Reference Level). A healthcare/day-care facility has heightened sensitivity — long dwell times, vulnerable users. If radon membrane is required by Arch, the structural slab buildup, sealing details around penetrations (drainage stacks, services), and edge details (rising wall junction) must be coordinated with the structural detail, including radon sump if needed. Currently the responsibility is silently passed to Arch. | Confirm Fingal/Swords radon classification with current RPII map; if high-radon, require full radon barrier + radon sump + service-penetration sealing per BRE Report BR 211 and detail same on the structural slab section. Coordinate with Architect's slab/wall junction detail. Reflect responsibility in Ancillary Designer Cert matrix. | 11002 typical slab section: '1200 Gauge Visqueen grade A (or DPM/Gas barrier to Arch's Details) on 150 mm Compacted Hardcore Sub-Base ...' | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\11002 - GROUND FLOOR PLAN.pdf | CS_DESIGNER | OPEN
S-027 | MEDIUM | C&S | COORDINATION | RC0000 RC Keyplan + RC0001-0007 (RC sheets) vs Arch partition plans | Whole keyplan | BCAR coordination; Fire Report Condition 3 (compartment walls); EN 1992-1-1 cl. 6 (service penetrations); IS 3218 / IS EN 12845 (any sprinklers). | RC keyplan (RC0000) and RC sheets 01-07 detail the RC beams/walls but do not show: (a) M&E service penetrations through structural elements (compartment-line walls per Fire Condition 3 require fire-rated penetration seals); (b) ductwork penetration sizes pre-formed; (c) coordination markers with Arch partition plans (some 250 RC walls are likely on Arch partition lines but no cross-ref). Penetrations cored after the fact compromise structural capacity and fire compartmentation. | Coordinate a 'Builder's Work in Concrete (BWIC)' overlay drawing showing all M&E penetrations >100 mm dia. through RC walls/beams/slabs with sleeve schedule and rebar trimming detail. Issue as a new C&S sheet or as an M&E coordination sheet. Cross-reference fire-stopping seal specification. | RC0001 shows BEAM 01-06 and BEAM 11 plan and sections — no BWIC penetrations shown on any RC sheet. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\RC0001 - RC SHEET 01.pdf | CS_DESIGNER | OPEN
X-011 | MEDIUM | CROSS-DISCIPLINE | CONTRACT | Whole pack — PSDP appointment / Preliminary Health & Safety Plan | Site Demolition Plan AR-10002; Site Setup Plan AR-10003 | SI 291/2013 Safety, Health and Welfare at Work (Construction) Regulations 2013 Reg 9 (PSDP appointment by client at design stage); HSA Code of Practice for Construction PSDP; CWMF Pillar 1 Stage 2C (Preliminary H&S Plan as Stage 2 deliverable) | Pack includes Site Setup Plan and Site Demolition Plan (AR-10002, AR-10003) but no Preliminary Health & Safety Plan is included as Appendix to the tender pack and no PSDP appointment is identified in any specification. Under SI 291/2013 the Client (HSE / CRC Omni) is legally responsible for appointing a PSDP at design stage and the Preliminary H&S Plan is a tender-pack deliverable that bidders must price the Construction Phase H&S Plan against. An existing-building demolition element creates a duty for an asbestos R&D survey under the Asbestos Regulations (SI 386/2006) — not referenced in pack. Without these, the contract is not a complete pre-tender H&S package. | Pre-tender: ER to (a) confirm PSDP appointment in writing and name them in Tender Volume 1, (b) include Preliminary H&S Plan as Tender Appendix, (c) commission and include asbestos R&D survey (or written confirmation that no demolition involves pre-2000 fabric), (d) include existing utilities survey reference (ESB, GNI, Irish Water mains in vicinity). | Pack manifest contains 'Site Survey & Site Demolition Plan' (AR-10002) and 'Site Setup Plan' (AR-10003). Grep across all specifications for 'PSDP' / 'preliminary health and safety plan' / 'principal designer' returns only Arch Spec line 9252: 'Refer to any pre-existing CDM Health and Safety File' — a UK-CDM reference, not the Irish SI 291/2013 equivalent. Asbestos R&D survey not referenced. | Whole pack — PSDP appointment / Preliminary Health & Safety Plan | PSDP — To be confirmed / Employer to appoint | OPEN
X-012 | MEDIUM | CROSS-DISCIPLINE | PROGRAMME | Pack manifest — CWMF Pillar 1 Stage 2 deliverables | Whole pack | CWMF Pillar 1 (Design + Procurement) Stage 2 deliverables; HSE Capital Project Manual (HSE PCM) Phase 2; DPER Public Spending Code (Programme + Cost certainty before tender) | Stage 2C under CWMF requires: (a) Stage 2 Design Report, (b) Stage 2 Cost Report (to within 10% of construction cost), (c) Project Programme (Gantt) to detailed-design milestones, (d) Risk Register, (e) Planning Permission grant, (f) FSC grant, (g) DAC grant. Pack delivers (a) design package, (e) planning and (f) FSC. Cost Report, Programme, Risk Register and DAC grant evidence not visible in pack root or as discrete appendices. Tender issuance without a current Cost Report (within DPER tolerance) risks Public Spending Code non-compliance and audit exposure. Programme absence prevents contractor making informed Section 1.1 commitments under PW-CF5 (Time for Completion / Sectional Completion). | Pre-tender: QS to deliver up-to-date Cost Report; ER to deliver Programme and Risk Register; Employer to deliver DAC grant (or confirm not required per occupancy class). Each appended as Tender Volume 2 schedule. If any of these is genuinely outstanding, treat as a CWMF Stage Gate failure and escalate to the Project Board before issuing tender. | Pack manifest (Stage 2C) contains Appendices A (Arch), B (C&S), C (M&E), E (Fire). No Appendix D = Cost Report. No project programme document. No Risk Register. No DAC grant evidence (only FSC grant referenced). | Pack manifest — CWMF Pillar 1 Stage 2 deliverables | EMPLOYER — HSE PCM Project Manager / CRC Omni | OPEN
X-013 | MEDIUM | FIRE/COORDINATION | COMPLIANCE | Fire Compliance Report §9 (cause-and-effect); Elec Spec §12 (alarm cabling); Mech Spec (HVAC shutdown) | Cause-and-effect matrix | IS 3218:2024 §11 (cause and effect); BS 7273-4:2015; BS 9999:2017 §17.8 (interface with HVAC); TGD-B Vol 2 (2024) §B1.4 (means of escape) | Fire Compliance Report §9 states 'Cause and effect of access control proposal reviewed and agreed based on the principals of IS EN 13637 2015 … Types of systems and ironmongery are yet to be approved.' That last sentence (Sept 2025) is unresolved at tender issue eight months later. The cause-and-effect matrix is not formally appended to the tender pack — it exists as a screenshot in the Fire Report. The bidder cannot integrate the access control sub-contractor with the fire alarm contractor without a formal C&E document covering at minimum: (i) detector / call-point input zones, (ii) sounder/VAD outputs, (iii) mag-lock release commands, (iv) hold-open release commands, (v) AHU shutdown, (vi) kitchen suppression discharge → gas valve close → extract fan shutdown → alarm input, (vii) PV isolator status (per Elec Spec §13 fire-officer switch), (viii) lift homing (if any), (ix) refuge intercom power retention. | Pre-tender: ORS Fire to issue a formal Cause-and-Effect Matrix as an Appendix to the Fire Compliance Report (signed). T5 Elec to reference this matrix in Elec Spec §12 and require the fire-alarm sub-contractor to deliver the matrix-driven commissioning. T5 Mech to reference it in HVAC controls section. This single document closes a 1.5 day commissioning ambiguity later in the programme. | Fire Report §9: 'Cause and effect of access control proposal reviewed and agreed based on the principals of IS EN 13637 2015 and are outlined in the screenshot below. Types of systems and ironmongery are yet to be approved.' [screenshot referenced in report but not externalised as formal C&E matrix to tender pack] | Fire Compliance Report §9 (cause-and-effect); Elec Spec §12 (alarm cabling); Mech Spec (HVAC shutdown) | ER — ORS Fire (issue) + T5 (incorporate) | OPEN
X-014 | MEDIUM | CROSS-DISCIPLINE | OPERATIONAL | Architectural FF&E / hoist track; Elec containment; C&S Roof Plan / ceiling structure | Therapy / changing / shower areas; hoist track coordination | HBN 00-04 (Circulation and access spaces); HBN 00-02 (Sanitary spaces); HSE PCM equipment schedule for accessible bathrooms; LOLER (Lifting Operations and Lifting Equipment Regulations transposed via SI 299/2007 General Application Regs Part 4) | Pack includes Changing Room and Shower Room laid-to-falls details (AR-53001, AR-53002) and FF&E schedule (AR-40008) for a disability day-care centre, but there is no Hoist Track Layout drawing, no structural confirmation of ceiling host capacity for hoist tracks (typically 2 kN point loads at track ends), and no Elec spec callout for hoist drive units' power supply and charging. CRC Omni's client cohort routinely includes wheelchair-users requiring transfer — absence of designed hoist provision is a clinical and HIQA risk. Three-discipline gap (Arch — track layout, C&S — ceiling capacity, Elec — power + battery charging point). | Pre-tender: ER to obtain CRC Omni clinical user-requirement statement on hoist provision (yes/no per room — accessible WC, changing rooms, shower rooms, group therapy rooms). If yes, Architect to issue Hoist Track Layout, Kavanagh Mansfield to confirm structural ceiling/roof loading, T5 Elec to issue power schedule, and Mech to confirm no clash with HVAC supply terminals in track sweep zone. If no, document the clinical decision in the Design Report for HIQA visibility. | Pack contains 'AR-53001 Changing Room - Laid to Falls', 'AR-53002 Shower Room - Laid to Falls', 'AR-40008 Architectural FF&E Components - Totals'. Grep across full Architectural + C&S + Elec + Mech specs for 'hoist' returns no design entries (only Mech 'hoist' references appearing in generic plant install clauses). | Architectural FF&E / hoist track; Elec containment; C&S Roof Plan / ceiling structure | EMPLOYER — CRC Omni clinical lead via ER | OPEN
X-015 | MEDIUM | FIRE/COORDINATION | DOCUMENT_HYGIENE | Fire Compliance Report cross-reference to architectural pack drawings | Drawings list | SI 9/2014 Code of Practice §2.5 (designer to coordinate documents); RIAI Conditions of Engagement §3.5 (design coordination) | ORS Fire Report references 'Drawing No. 22481-PFD-XX-00-DR-F-003 Proposed Floor Plan' (ORS-originated FSC drawing) as the master fire plan, while the Architectural Wall & Partition Types drawing AR-15001 references 'Fire Cert, Drawing No. 1000A, 1001A & 1002A' — a third numbering system. The tender pack therefore relies on THREE different drawing numbering conventions for fire compartmentation (ORS PFD-series, Rhatigan 1000A series, Rhatigan AR-15001 series). Risk: the contractor builds to the wrong one and the Assigned Certifier rejects at site inspection. Document-hygiene issue with compliance teeth. | Pre-tender: Architect to issue a single 'Fire Strategy Drawing' (AR-90xxx series suggested) consolidating compartment line geometry, door types, escape routes, refuge zones, fire-alarm zone boundaries and access-control overrides — formally cross-referenced from both ORS Fire Compliance Report AND the AR-15001 partition types AND the Door Schedule AR-40001. Mark superseded drawings (PFD-series, 1000A series) clearly as 'For FSC submission only — not for construction'. | Fire Report §1: 'Drawing Number 22481-PFD-XX-00-DR-F-003 Proposed Floor Plan'. Wall & Partition Types AR-15001 legend: 'Fire Rating: Refer to Fire Cert, Drawing No. 1000A, 1001A & 1002A'. Internal Door Schedule AR-40001 General Note F: 'Drawings to be read in conjunction with fire compliance report & all other contract documents'. | Fire Compliance Report cross-reference to architectural pack drawings | LEAD_DESIGNER — Rhatigan (lead) + ORS Fire | OPEN
X-016 | MEDIUM | FIRE/COORDINATION | COMPLIANCE | Boundary walls — 1500 mm and 1800 mm brick walls on site plan | C&S Boundary Wall Details 50001; Fire Report (boundary references) | TGD-B Vol 2 (2024) §B4 (external fire spread — boundary distances); TGD K (Stairs, Ladders, Ramps and Guards — boundary heights for safety); BS 9999:2017 Annex D (boundary distance calculation) | Site has boundary walls at 1500 mm and 1800 mm — these are critical for (a) Part B unprotected area calculation (relevant boundary), (b) Part K guarding where there is a level change either side of the wall, (c) overlooking / privacy under planning (HIQA dignity). The C&S Boundary Wall Detail 50001 is a structural detail; coordination with Fire's unprotected area calculation and Arch's elevation drawing (AR-20001) needs an explicit Boundary Distance Schedule showing each external face → relevant boundary distance → permitted unprotected area % → actual unprotected area % from window/door schedule. Single-page schedule typically missing in Stage 2 packs and often surfaces as a fire-officer revised FSC trigger. | Pre-tender: ORS Fire to issue a Boundary Distance + Unprotected Area Compliance Schedule (one row per external elevation), cross-referenced to Arch Window & External Door Schedule AR-40002 and to the Site Plan / Elevations AR-20001. Kavanagh Mansfield to confirm 1500/1800 mm boundary wall structural design accounts for any retained earth or wind loading from neighbour-side level changes. | Pack C&S drawings list includes '50001 - 1-8 m Boundary wall details.pdf' (height range suggests multiple wall heights). Fire Compliance Report references boundary walls in cause-and-effect plan (per brief). No Unprotected Area Schedule appended to Fire Report or to Arch elevations. | Boundary walls — 1500 mm and 1800 mm brick walls on site plan | ER — ORS Fire + Rhatigan + Kavanagh Mansfield (coordinate) | OPEN
A-007 | LOW | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Drawing Register | AR-40010 Ironmongery & Access Control Plan & Schedule | Register accuracy | Spelling error 'Inronmongery' on controlled register. | Correct spelling to 'Ironmongery'. | Register p.1: '11606-XX-XXX-SH-RHA-AR-40010 Inronmongery & Access Control Plan & Schedule'. | 11606-RG-RHA-AR-0001 Drawing Register p.1 | ARCH_DESIGNER | OPEN
A-008 | LOW | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Drawing Register | Legend for issue type codes (p.2 bottom) | Documentation hygiene | Letter 'P' is used twice in the issue type legend — once for 'paper' format and once for 'planning' issue purpose. Single character collision creates ambiguity. | Use 'PL' for planning issue (or 'PP' for paper planning) to remove collision. | Register p.2: 'P - paper / P - planning'. | 11606-RG-RHA-AR-0001 Drawing Register p.2 | ARCH_DESIGNER | OPEN
A-032 | LOW | ARCHITECTURAL | DOCUMENT_HYGIENE | Architectural Works Specification | Section Q37/130 - Bauder green roof | BS 1192:2007+A2:2016 §6.4 (Quality control / spell-checking of issued documents); RIAI SCE §5.2. | Q37/130/7 'Vegetation: BauderGREEN SB Sedum Blanekt' contains spelling error 'Blanekt' (should be 'Blanket'). Procurement search for the misspelt product will fail; orderer may select the wrong specie. Trivial but a marker of insufficient QA at issue. | Correct typo to 'Sedum Blanket'. Run a full spell-check pass before tender re-issue. | 7. Vegetation: BauderGREEN SB Sedum Blanekt | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf p.178 (Q37/130) | ARCH_DESIGNER | OPEN
A-036 | LOW | ARCHITECTURAL | CONTRACT | Architectural Works Specification | Front matter (Document Control Sheet) | PW-CF5 Sub-Clause 1.1 'Works Requirements'; RIAI Standard Conditions of Engagement; BS EN ISO 19650-2 §5.5 (Information Container Status Codes). | Spec front sheet reads 'Publication Status: Pre-Tender; Publication Revision: 0' and is dated 19-05-2026. Drawing schedules in the same pack carry Status 'P08-S' (Stage 2C Information Issue) dated 08-05-2026. Internal mismatch between spec status ('Pre-Tender') and drawing status code, with a 11-day gap. Tender package needs a consistent status (e.g., 'P09-T Tender Issue') across spec and drawings on a single Tender Issue date. | Update spec front sheet to 'Publication Status: Tender Issue (P09-T)' with date matched to tender issue (target 10-Jun-2026). Match drawing schedule revisions and status code at Tender Issue. | Publication Status: Pre-Tender / Publication Revision: 0 / Rhatigan + Company Ltd / 19-05-2026 [vs Schedule 40006 STAGE 2C STATUS P08 - S REV 0 DATE 08/05/2026] | 11606-ZZ-ZZZ-SP-RHA-AR-91011 Architectural Works Specification.pdf front matter; 11606-XX-ZZZ-SH-RHA-AR-40006 title block | ARCH_DESIGNER | OPEN
A-128 | LOW | ARCHITECTURAL | DOCUMENT_HYGIENE | GA Plan Drawing Notes — duplicate/mis-numbered lettering | Drawing 11001 + most arch sheets | CWMF document control | All arch sheets have two notes labelled 'E.' and two labelled 'F.' in the Conditions of Use of this Drawing block (E. fire stopping note appears twice; F. drawings to read with fire... AND F. comply with H&S Act). Numbering integrity error throughout pack. Minor but propagates through document control register. | Re-letter Conditions of Use of this Drawing notes consecutively (A–K) on title-block template; reissue master template + all sheets at next revision. | 11001 / typical title block: 'E. All fire stopping...' followed later by 'E. All works to be carried out... including for all other I.S, B.S...' and 'F. Drawings to be read in conjunction with fire compliance report...' followed by 'F. All works to comply with Health & Safety Act.' | All Arch drawings | ARCH_DESIGNER | OPEN
E-019 | LOW | ELECTRICAL | Bill of Quantities / Duplications and Er | Electrical Specification + drawings | Bill items duplicated and mis-numbered (68-13 duplicates 68-11; 68-06 missing; M-02 duplicated; 65-05 missing) | Tender document integrity / PW-CF5 fair tender process. | Tenderer confusion. Price duplications or omissions. Risk of bid being non-compliant. | Issue tender addendum: renumber bill items consistently (no gaps, no duplicates). Delete 68-13 duplicate. Decide whether 68-03/68-04 are intentionally duplicated (e.g. for two separate panels) and label accordingly, or delete one. Renumber 68-06 onwards. Fix M-02 duplication. | Bill 68-11: 'Complete supply, installation and testing of Disabled Refuge System as indicated on the drawings including interfacing them with the Fire Alarm.' Bill 68-13: 'Complete supply, installation and testing of Disabled Refuge System as indicated on the drawings including interfacing them with the Fire Alarm.' [IDENTICAL DUPLICATE]. Bill 68-06 missing (jumps 68-05 to 68-07). Bill 68-03 and 68-04 are word-for-word identical ('Complete installation of Intruder Alarm Equipment to include intruder alarm panel, passive infrared detectors, door and window contacts.'). M-02 used twice (Insurances AND H&S at Work). Bill 65-05 missing (jumps 65-04 to 65-06). | Spec: Bill (M), Bill (65), Bill (68) | EE_DESIGNER | OPEN
E-021 | LOW | ELECTRICAL | Obsolete Telecoms / Future-Proofing | Electrical Specification + drawings | Telecoms cabling spec §5.08 specifies 'Systimax PDS1010 LAN cable' (legacy Cat 5e, EOL ~2005), and references 'Eircom' / 'Eir telephone-monitoring network' | Healthcare ICT infrastructure typically Cat 6A (10GBASE-T headroom). HSE ICT standards. Fire alarm signalling - I.S. 3218:2024 Annex / EN 50136 series Alarm Transmission Systems (move to dual-path IP+GSM). | Inconsistent data cable spec (PDS1010 in §5.08 vs Cat 6 in bill 62-08 vs Cat 6A in §5.10 and bill items). Eir PSTN end-of-life will affect fire alarm monitoring path. HSE may require Cat 6A throughout for clinical comms future-proofing. | Issue tender addendum: rewrite §5.08 to harmonise with bill 62-08 - 'Cat 6A F/UTP LSZH to ISO/IEC 11801, terminated to TIA-568-C.2 - all data and voice outlets'; confirm with HSE ICT whether Cat 6A required. Replace Eir/Eircom references in §12.11/12.12 with: 'dual-path Alarm Transmission System (ATS) to EN 50136-1 Cat SP4/DP3 minimum, IP + GSM/4G paths, signalling per I.S. 3218:2024'. Provisional sum for ARC monitoring contract (first year). | Spec §5.08: 'Internal telephone cables shall be of the multicore type for main distribution and four pair for local circuit from junction boxes to outlets. They shall have copper conductors 24 A.W.G., insulated suitable for voice and data 16 MIPS transmission type Systimax PDS1010 LAN cable.' '16 MIPS' is Cat 5e era. Bill 62-08 specifies 'CAT 6 data cabling' - inconsistent with §5.08. §5.10 CCTV uses 'Cat 6 A'. Fire alarm signalling §12.11/12.12 references 'Eircom' / 'Eir telephone-monitoring network' - PSTN signalling is being decommissioned by Eir (PSTN switch-off; ARC monitoring now IP/4G). | Spec: §5.08, §5.10, §12.11, §12.12, Bill 62-08, Bill 62-09 ¦ Drawings: 1743_62(00), 1743_68(00) | EE_DESIGNER | OPEN
E-023 | LOW | ELECTRICAL | Project Hygiene / Misc Errors | Electrical Specification + drawings | Misc minor errors: VAT shown as 21% (should be 23% standard Irish rate since 2014); Aspirating detection §12.21 ('AirSense', 'ModuLaser' - unusual for a 867m² day-care unless specific need); EMC Directive cited as 89/336/EEC (superseded by 2014/30/EU) | Irish VAT Acts (standard rate 23% since 2014, with temporary reductions during COVID-19 reversed by 2024); EMC Directive 2014/30/EU; Gas Networks Ireland Code of Operations; Construction Workers Pension Scheme. | VAT calculation could be wrong in tender returns. EMC compliance citation outdated. Bord Gais reference confuses tenderers. CWPS reference incorrect. Aspirating detection may or may not be required - tender ambiguity. | Issue tender addendum: (1) Change VAT 21% to 23% (or current Irish rate); (2) Update EMC Directive citation to 2014/30/EU; (3) Replace 'Bord Gais' with 'Gas Networks Ireland'; (4) Replace 'Loss Prevention Council' with current ATC monitoring body (e.g. BRE Global/RC); (5) Replace 'C.I.F. Pension/Sick Pay scheme' with 'CWPS - Construction Workers Pension Scheme'; (6) Confirm aspirating detection requirement with HSE clinical brief - if not required, delete §12.21 and Bill 68-15; if required, identify the rooms it covers (likely none for a day-care with no high-value computer suite). | Spec MAIN SUMMARY: 'VAT @ 21 %' (line 7). Spec §2.05 Standards: 'The EMC Directive 89/336/EEC' (superseded by 2014/30/EU). Spec §12.21 specifies aspirating smoke detection (AirSense, ModuLaser, APIC) - typically used in high-risk/clean room/computer suite/cold store environments, not standard day-care. Bill 68-15 'Aspiration System' - if required, scope must be defined; if not required, delete. Spec §3.13 references 'Bord Gais' (rebranded Gas Networks Ireland 2014). Spec §2.05 lists 'Loss Prevention Council Rules' (defunct UK insurance body merged into BRE). Spec §3.13 references 'Health & Safety at work Act' without year. §3.30 references 'C.I.F. Pension/Sick Pay scheme' (CWPS - Construction Workers Pension Scheme since 2018). | Spec: §2.05, §3.13, §3.30, §12.21, Bill 68-15, MAIN SUMMARY VAT line | EE_DESIGNER | OPEN
E-024 | LOW | ELECTRICAL | Drawings Index / Document Hygiene | Electrical Specification + drawings | Drawing register §1.0 mismatches between schedule and actual file names; hyphen vs underscore inconsistency '1743_63-01.pdf' vs '1743_63 (01)' - aligns with M-004 hygiene flag | BCAR Code of Practice for Compliance with Building Regulations - drawing register accuracy; CDE / ISO 19650 naming conventions. | Drawing references in spec body don't match filenames - tender clarifications required. EDMS/CDE upload may fail validation. Reinforces M-001 to M-004 hygiene findings. | Issue tender addendum: rationalise drawing naming convention (recommend underscore + 2-digit suffix: '1743_63_00.pdf') and reissue all drawings with consistent names AND update spec §1.0 to match. Rename spec PDF to remove typo ('Electrical Specification.pdf') and trailing space. Coordinate with M-001/M-004. | Spec §1.0 lists drawings with format '1743_63 (00) General Lighting' and '1743_63 (01) Emergency Lighting'; actual file in directory is '1743_63-01.pdf' (hyphen instead of underscore-bracket). Mix of '1743_60(00)' inline-bracket and '1743_63 (00)' space-bracket and '1743_63-01' hyphen formats. Filename of spec itself 'Electrical Specifiction .pdf' (sic - typo + trailing space). | Spec: §1.0, Filename of spec ¦ Drawings: All 1743_* electrical drawings | EE_DESIGNER | OPEN
E-120 | LOW | ELECTRICAL | DOCUMENT_QUALITY | Drawing register 1743_63-01 vs 1743_63_00 | Naming convention | PW-CF5 §1 Tender documentation completeness | Drawing 1743_63-01.pdf uses dash, while 1743_63_00.pdf uses underscore. The spec drawing schedule §1.0 lists both as '1743_63 (00)' and '1743_63 (01)' with space. Three different naming conventions for the same drawing series. Risk: contractor downloads wrong revision; clarification queries during tender period; missed drawings in BoQ pricing. | Adopt single consistent naming convention: '1743_63_00.pdf', '1743_63_01.pdf' (underscore, no space). Re-issue Drawing Register table with corrected filenames. Confirm all files on eTenders match register exactly. | Filename '1743_63-01.pdf' [dash], filename '1743_63_00.pdf' [underscore]; spec §1.0 lists '1743_63 (00) General Lighting - Ground Floor', '1743_63 (01) Emergency Lighting - Ground Floor' [space + bracket] | Electrical Drawings folder; Electrical Specification .pdf | EE_DESIGNER | OPEN
E-121 | LOW | ELECTRICAL | DOCUMENT_QUALITY | Electrical Specification | §2.05 / Multiple | PW-CF5 §3 Specification Quality; Construction Industry best practice | Spec contains numerous obsolete or non-Irish references additional to those flagged above: 'EMC Directive 89/336/EEC' (superseded by 2014/30/EU), 'BS 4293' (RCDs — superseded by I.S. EN 61008/9), 'BS 5839 part 2' (UK fire-alarm code), 'V.D.E. 0641/6.78' (German MCB standard from 1978), 'BS 3676 1989' (light switches — superseded by I.S. EN 60669), 'B.S. 6004:1975', 'BS 4678 Part 1' (cable trunking — superseded by I.S. EN 50085), 'B.S. 89/IEC 51' (analogue meters), 'BS 3938' (CTs — superseded by IEC 61869), 'B.S. 6346:1989' (cables — superseded by I.S. EN 50525), 'BS 8724:1990' (cables), 'IEC 144' (replaced by IEC 60529), 'Eircom' (rebranded eir 2014/Vodafone Three). Also page headers say 'Mechanical Services Specification' on pages 3–10 of an Electrical Spec. | Comprehensive standards refresh — replace every obsolete BS/IEC/VDE reference with current I.S. EN equivalent. Replace 'Eircom' with 'open-access telecoms operator' or 'incumbent network operator'. Fix page headers from 'Mechanical' to 'Electrical Services Specification' on pages 3–10. Add document version control footer with revision number and date. | §2.05 'BS 7671:2018... EMC Directive 89/336/EEC'; §4.18 'BS 4293 or CEE19'; §4.19 'BS EN 60898, 1991' [year-frozen]; §10.05 'B.S. 3676 1989'; §10.07 'Legrand 0600 77' [single-source]; §12.02 'Morley Apollo'; §10.04 'Apollo loop'; multiple pages headed 'T5 Partnership Ltd. Tender Issue – Mechanical Services Specification' in an Electrical spec | Electrical Specification .pdf | EE_DESIGNER | OPEN
H-022 | LOW | HEALTHCARE | TYPO_ROOM_NAME | 11606-XX-L00-DR-RHA-AR-11001 GA Plan (and signage) | Room 0.32 Meeting & Consultation | Pack quality and consistency for tender issue. | Brief lists Room 0.32 as 'Meeting & Consulation' (sic). GA plan AR-11001 spells it correctly as 'MEETING & CONSULTATION' so the typo is only in the brief. Low risk — flag for register only. No action required if drawing spelling is consistent across signage AR-17001 (verified correct in this review). | No action required on the design. Update internal brief/register only. Confirm Signage Schedule AR-17002 (Sheet 1) carries the correct spelling on Room ID sign. | AR-11001 GA Plan: 'MEETING & CONSULTATION 0.32 22.25 m²'. AR-17001 Signage Plan: 'MEETING & CONSULTATION 0.32'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix A - Architectural\Drawings\11000_GA Plans\11606-XX-L00-DR-RHA-AR-11001- GA Plan - Ground Floor.pdf | ARCH_DESIGNER | CLOSED
M-004 | LOW | M&E | DOCUMENT_HYGIENE | M&E Electrical Specification filename | File name | Document hygiene | Spec file is named 'Electrical Specifiction .pdf' (typo + trailing space) instead of 'Electrical Specification.pdf'. CDE search and version control compromised. | Rename file to 'Electrical Specification.pdf' on issue. | Pack file path: 'Appendix C - Mechanical and Electrical/Electrical Specifications/Electrical Specifiction .pdf'. | Pack manifest | ME_DESIGNER | OPEN
M-024 | LOW | MECHANICAL | Spec hygiene / quality control | Mechanical Specification.pdf | Spec section numbering errors — duplicate '4.34', '4.35', '4.36', '4.41'; section '11.02/11.03/13.0' renumber jumps; '56-03/56-04/56-05' Bill items duplicated | PW-CF5 Clause 2 (contract documents must be unambiguous) | Ambiguity at tender, post-tender claims risk, professional appearance. | Full QC sweep on numbering before Tender issue. | Spec has duplicate clause numbers: §4.34 appears twice (Strainer / 2-Port Valves), §4.35 twice (Commissioning Valves / Strainer), §4.36 twice (Hydrocyclonic Filters / Pipework jointing), §4.41 twice (Valves Fittings / Control Valves). §11.02 and §11.03 jump back to §13.0 Fire Fighting. BoQ §56-03 / 56-04 / 56-05 appear twice with different scope (Hot Water Generator vs Heating timeclock and pipework). | Mechanical Specification.pdf §4 (multiple) ¦ Mechanical Specification.pdf §11 / §13 ¦ Mechanical Specification.pdf BoQ §56 | ME_DESIGNER | OPEN
M-025 | LOW | MECHANICAL | Spec hygiene | Mechanical Specification.pdf | Spec typos and historical references (COVID-19 SOPs, 1969 standards, 1972 standards) suggest stale base document not refreshed for May 2026 Tender Issue | PW-CF5 Clause 2; professional QC | Spec is a recycled template — reduces tenderer confidence and creates risk that other clauses (less obvious) are also stale. Engineering Council CEng ethics: signed-off document should be of professional quality. | Designer to perform proof-reading sweep before Tender issue; remove COVID-19 clauses; align electrical references to I.S. 10101. | Spec Tender Issue date 'May 2026_Tender' but Form of Tender §17 still references 'Construction Industry Federation's Standard Operating Procedures issued with respect to the COVID-19 Pandemic'. Multiple typos: 'within exposed at roof level', 'minimu9m', 'mini9mum', 'pirework trace', 'one peace tank', 'capabity', 'be hwn'. Reference to 1969 BS 4504, 1972 BS 476-8, 1982 BS 2989, 1980 IS 238. Reference to 'BS 7671:2018' but I.S. 10101:2020+A1:2024 is the Irish wiring rule. | Mechanical Specification.pdf §17 (COVID-19 clause) ¦ Mechanical Specification.pdf §10.07 (typo), §6.04 (typo) | ME_DESIGNER | OPEN
M-026 | LOW | MECHANICAL | TGD L / NZEB | Mechanical Specification.pdf | Heating energy / BER NZEB compliance check not evidenced — Part L primary-energy and renewables share calculation not in pack | TGD L 2022 (Conservation of Fuel and Energy — Buildings other than Dwellings); SI 183/2019 Building Regulations Part L Amendment; EPBD (recast) Directive (EU) 2018/844 | Risk of failing Part L NZEB at BCAR Stage 3 (commencement) without a provisional NEAP. Healthcare day-care is non-domestic — minimum A3 / A2 target. | Designer (Energy Rating Assessor — T5 advertises this discipline) to issue provisional NEAP / DEAP-NonDom output with renewables share, primary energy and target BER. Bind into tender pack to give tenderers visibility on the Part L target they are inheriting. | Spec §9.02 SCOP minimum 4.45 stated, but no Part L calculation, no renewables share %, no Primary Energy / Primary Energy Renewable ratio, no MPCS / DEAP Non-Domestic / NEAP output, no BER provisional rating. Spec §2.05 standards list does not include TGD L. Spec §9.02 cites 'Compliant with: ErP Directive 2009/125/EC and ELD 2010/30/EC' — ErP is product-level only, not building-level. | Mechanical Specification.pdf §9.02 ErP Directive reference ¦ Mechanical Specification.pdf §2.05 Standards list (no TGD L) | ME_DESIGNER | OPEN
M-120 | LOW | MECHANICAL | SCOPE_NA | Mech Spec §8.03 + §9.09 | Medical gases, natural gas, gas detection | HTM 02-01 (medical gas pipeline systems); IS 820 (gas installations); IGEM standards | Spec confirms §8.03 Incoming Natural Gas 'N/a' and §9.09 Gas Detection 'N/a'. Confirmed all-electric building (no IS 820 gas works). Medical gases (O2, vacuum, medical air) not mentioned anywhere in spec — this is correct for a day-care under HBN 12 / HBN 23 (no clinical procedures); however, suggest explicit confirmation in spec scope so contractor does not price out medical-gas allowances by exception. Low-severity housekeeping. | Add single-line statement in §1 scope: 'No medical gas pipeline systems (HTM 02-01) are included. No natural gas (IS 820) is included. Building is all-electric per CRC and HSE day-care brief.' | Mech Spec §8.03.1 'N/a'; Mech Spec §9.09 'Gas Detection: N/a'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix C - Mechanical and Electrical\Mechanical Specifications\Mechanical Specification.pdf | ME_DESIGNER | OPEN
S-006 | LOW | C&S | DOCUMENT_HYGIENE | C&S Drawing Register (DR01) | Drawing 50002 title | Register accuracy | Spelling error 'REAR RETAINING WALLll' (double 'll' suffix). Controlled register accuracy. | Correct to 'REAR RETAINING WALL'. | DR01: '50002 — REAR RETAINING WALLll'. | DR01 - DRAWINGS REGISTER.pdf | CS_DESIGNER | OPEN
S-007 | LOW | C&S | DOCUMENT_HYGIENE | C&S Drawing Register (DR01) | Project identification block | Project coherence | C&S register identifies project as '57 RATHBEALE ROAD' only — no project number reference (Arch uses 11606, M&E uses 1743). Cross-discipline cross-reference broken. | Add Arch project reference number (11606) to C&S register title block for cross-discipline traceability. | DR01 title block: 'Project: 57 RATHBEALE ROAD' — no project number. | DR01 - DRAWINGS REGISTER.pdf | CS_DESIGNER | OPEN
S-025 | LOW | C&S | QA | Specification cover sheet | Section list | BCAR documentation completeness; PW-CF5 tender requirements. | Spec contents list contains Sections A, B, C, E, F, H, M2, P, SD, SR, SW — Section D (Demolition / specific) and Section AB / AA are absent. Section D is referenced elsewhere in the standard KMP boilerplate as Materials & Workmanship. Section G (Drainage above ground) is absent. While not all sections are needed for every project, the absence should be explicit so the contractor knows nothing is missing inadvertently. | Add a note on the cover sheet 'Sections D, G, J, K, L, M1, N (etc.) are not applicable to this project.' This avoids tenderer queries. | Cover sheet lists: 'Section A ... Section B ... Section C ... Section E ... Section F ... Section H ... Section M2 ... Section P ... Section SD ... Section SR ... Section SW'. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SPECIFICATION\Specifications - Rathbeale Rd.pdf | CS_DESIGNER | OPEN
S-028 | LOW | C&S | COMPLIANCE | 12001 Proposed Drainage | Hardstanding / vehicular area drainage points | GDRCoP / Fingal Water Pollution Control bye-laws; Building Regulations TGD H4; EPA water quality standards; oil interceptor BS EN 858-1 (Class I/II separator). | Drainage plan shows surface water collection but does NOT depict any oil/petrol interceptor (Class I Bypass or Full Retention separator) on the surface water network upstream of the hydrobrake. The site includes vehicular hardstanding (drop-off, ambulance bay, staff parking visible on Arch site plan) which is a Polluting Surface under GDRCoP. Direct discharge to council SW system risks breach of bye-law and Fingal SW network pollution. | Add a Class I (full retention) oil/petrol interceptor on the SW collection line from any area receiving more than occasional vehicle traffic (>5 spaces), upstream of the hydrobrake and attenuation cell. Show on 12001 and add to the manhole schedule on 12005. | 12001 PROPOSED DRAINAGE shows SW01-SW11 manholes and 'Hydrobrake limited to 2 l/s' but no petrol/oil interceptor symbol or label. | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\12001 - PROPOSED DRAINAGE.pdf | CS_DESIGNER | OPEN
X-017 | LOW | CROSS-DISCIPLINE | DOCUMENT_HYGIENE | All specifications — standards-currency review | Spec headers referencing dated standards | SI 9/2014 BCAR (latest applicable standard at design freeze); RIAI / Engineers Ireland duty to design to current standards | Multiple specifications cite dated editions where a newer edition applies and is referenced by the granted FSC: Elec Spec line 3387 cites 'I.S 3218: 2013' vs FSC Condition 2 IS 3218:2024; Elec Spec line 3106 cites 'I.S. 3217: 2013'; numerous cross-spec entries say 'Latest Edition' generically. Bidders price the LOWEST interpretation of these terms ('Latest Edition' is loose — Latest at tender issue? at contract award? at handover?). Creates variation exposure under PW-CF5 Clause 4.5. | Pre-tender: Each designer to (a) replace generic 'Latest Edition' with explicit edition (e.g. 'IS 3218:2024'), (b) declare in spec front-matter the standards-currency cut-off date (recommend: 'Standards current as at 10-Jun-2026 tender issue date apply for construction'), (c) any later amendment to a standard during construction is dealt with under PW-CF5 Clause 1.6 (change in legal requirement). | Elec Spec line 3106: 'emergency lighting system in accordance with I.S. 3217: 2013 latest edition' [contradictory — '2013' and 'latest' both]. Elec Spec line 3387: 'I.S 3218: 2013'. Elec Spec line 455 and 1751: 'IS 3218 – Latest Edition' (without year). | All specifications — standards-currency review | LEAD_DESIGNER — Each discipline designer; coordination by Rhatigan | OPEN
E-012 | MED | ELECTRICAL | Obsolete Standards / Code References | Electrical Specification + drawings | Spec littered with withdrawn/superseded BS, IEC, VDE and brand standards (BS 5486, BS 5420, IEC 144, IEC 439, VDE 0641, BS 4293, BS 842, BS 1363:1984, BS 3676:1989, BS 4568-1970, BS 6004:1975, BS 6346:1989, BS 6360:1991, BS 7655, BS 8724:1990, ETCI 3rd Ed 2005/2006) | Standards cited shall be current at tender date per spec §3.5 itself ('Where Irish Standards/British Standards are referred herein these shall be deemed to refer to the current edition of such standards'). Tender practice and SI 9/2014 BCAR require current standards. | Suppliers cannot quote withdrawn standards. Tender ambiguity - is contractor required to comply with the obsolete standard cited verbatim or with §3.5 generic 'current edition' clause? Disputes inevitable. Items sourced from defunct manufacturers will fail QA review. | Comprehensive spec rewrite of §4, §5, §6 sections replacing withdrawn standards with current equivalents (full schedule on file): BS 5486/IEC 439 -> I.S./EN 61439; BS 4293 -> BS EN 61008/61009; BS 1363 -> I.S. 411 (Ireland); BS 6346/BS 7211 -> BS 7889 + BS 7846 + BS 6724; BS 7655 -> BS EN 50525; BS 5839 -> I.S. 3218:2024; BS 6360 -> BS EN 60228. Manufacturer references: Merlin Gerin -> Schneider; GEC -> Eaton or current equivalent; Klockner Moeller -> Eaton; Tube Rollers -> Marshall Tufflex or current Irish supplier. Brand references should be 'or equivalent' throughout (mostly already are). | Spec §4.02 lists 'BS 5486 Part I - Form 3' (withdrawn 1999, replaced by IEC/EN 61439); 'IEC 439' (withdrawn 2009); 'V.D.E. 0641/6.78' [§4.09]; 'BS 5420/IEC 144' [§4.05] (BS 5420 withdrawn 1996; IEC 144 replaced by IEC 60529); 'BS EN 60898 1991' [§4.17 §4.19] (current is BS EN 60898:2003+A13:2012); 'BS 4293' [§4.18] (withdrawn 2014); 'BS 842' [§4.18]; 'B.S. 1363-1984' [§8.03] (current BS 1363:2023, plus Irish standard is I.S. 411); 'BS 3676 1989' / 'B.S. 3676: 1963' [§10.05] (withdrawn 2003); 'BS 4568-1970' [§5.01] (withdrawn); 'B.S. 6004, 1975' / B.S. 6004 [§5.01 §5.04]; 'B.S. 6346:1989' [§5.02] (withdrawn 2009 replaced by BS 7889/BS 8436); 'BS 6360:1991' [§5.04 §5.05] (withdrawn 1992); 'B.S. 7655' [§5.04] (replaced by BS EN 50525); 'B.S. 8724: 1990' [§5.03] (withdrawn); 'BS 5839 Part 2' and 'BS 5839 Part 1 Latest Edition' [§12.09] (UK standards - in Ireland use I.S. 3218:2024). Manufacturer references obsolete: 'Merlin Gerin' [§4.09] (rebranded Schneider 1999); 'GEC Redspot' [§4.07] / 'GEC Measurements' [§4.12] (GEC sold off 1999); 'Klockner Moeller' [§4.20] (acquired by Eaton 2008); 'Tube Rollers Ltd.' [§5.01] (defunct). ETCI 'Third Edition Amendment No. 2 issued Sept. 2005' [§5.04] superseded by I.S. 10101:2008, then 2020+A1:2024. | Spec: §4.02, §4.05, §4.07, §4.09, §4.12, §4.13, §4.14, §4.17, §4.18, §4.19, §4.20, §4.22, §5.01, §5.02, §5.03, §5.04, §5.05, §5.07, §6.01, §8.03, §10.05, §10.06, §12.09 | EE_DESIGNER | OPEN
E-013 | MED | ELECTRICAL | Accessibility / TGD M | Electrical Specification + drawings | Socket outlets specified at '400mm AFFL' - non-compliant with TGD M 2022 which requires 450-1200mm AFFL accessible range | TGD M 2022 §3.13 Switches, Sockets and Controls: socket outlets 400-1000mm above floor for ease of reach by wheelchair users + general guidance 450mm minimum; switches 900-1200mm; BS 8300-2:2018 §10 same range with 25% rocker contrast and minimum 19mm rocker size. Healthcare day-care for users with mobility/cognitive impairment - higher 450mm minimum is recommended. | Statutory accessibility non-compliance. DAC risk. 400mm is below the TGD M Part M minimum reach band for sockets - wheelchair users with limited forward reach may not be able to use them. | Issue tender addendum: amend §8.03 socket outlet height to '450mm AFFL minimum to socket centreline (TGD M 2022 §3.13)'. Amend §10.05 light switch height to '900-1200mm AFFL; rocker switches minimum 19mm; contrasting plate per BS 8300-2:2018 §10' - already covered by §8.03 'high visual contrast' spec but extend to switches too. | Spec §8.03: 'Socket outlets shall be mounted generally at 400mm AFFL and 150mm above bench level.' Spec §10.05: 'Unless otherwise indicated, switches shall be mounted at 1200 mm. above F.F.L.' [boundary OK but no contrast/rocker size statement]. | Spec: §8.03, §10.05 ¦ Drawings: 1743_62(00) General Elec - check setting-out detail | EE_DESIGNER | OPEN
E-014 | MED | ELECTRICAL | Bonding / HTM 06-03 | Electrical Specification + drawings | Equipotential bonding section §7 minimal - no explicit supplementary bonding for wet areas, no medical location §710 cross-reference, no HTM 06-03 healthcare bonding | I.S. 10101:2020+A1:2024 §411, §415, §701, §710; HTM 06-03 (healthcare earthing); IEC 60364-7-710 (medical locations). | If any space is or becomes a Group 1 medical location (e.g. physiotherapy with body-touching equipment), Section 710 requirements apply (Equipotential Bonding Reference Bar in clinical room, supplementary bonding, IT system supplementary requirement). Spec gives no scope for this. Risk of post-occupancy electrical safety incident with vulnerable users. | Issue tender addendum: (1) Confirm with HSE clinical brief whether any room is a Group 1 medical location (any therapy with applied body parts) - if yes, expand §7 with §710 supplementary bonding plan and provisional sum; (2) Add explicit §7.05 'Supplementary Bonding - Locations Containing Bath/Shower' per §701 listing relevant rooms (accessible WCs); (3) Reference HTM 06-03 for healthcare context; (4) Specify earth fault loop impedance test thresholds and earth electrode resistance limit (typically <100 ohm separated for LPS or <10 ohm where TT) and require values to be recorded on Completion Cert. | Spec §7.03 Main Equipotential Bonding: brief generic clause stating 'install main and local equipotential bonding systems to comply with the requirements of NSAI Regulations Latest Edition.' No explicit reference to: (a) I.S. 10101 §701 (locations containing bath or shower - applies to accessible WC with shower, staff WCs, any shower); (b) I.S. 10101 §710 medical locations (relevant if any therapy room is Group 1 medical location - HSE clinical brief required); (c) HTM 06-03 (Earthing and bonding for healthcare); (d) supplementary bonding cross-sections for accessible WCs serving wheelchair users; (e) earth electrode resistance value/test; (f) earth fault loop impedance target by circuit type; (g) bonding for metallic ductwork/pipework at boundary of compartments. | Spec: §7.01, §7.03, §7.04 ¦ Drawings: 1743_60(01) Below Ground Services - earth electrode | EE_DESIGNER | OPEN
E-015 | MED | ELECTRICAL | Access Control / FSC Note 9 / I.S. EN 13 | Electrical Specification + drawings | Access control section §12.15 lacks coordination detail with Fire report Note 9 cause-and-effect (BGU, 15-second time delay, maglock Grade 1, IS EN 13637:2015 specifically) | I.S. EN 13637:2015 (Electrically controlled exit systems); FSC report Note 9 (cause and effect agreed); TGD B 1.1.7 escape; BS 8300-2 accessible exits. | Tenderers cannot price correctly - 15-second time delay devices cost more than standard maglocks. BGU grading not specified (Grade 1 per Fire report). Risk of installing wrong access control class - safety/escape compliance failure. Coordination gap with Arch ironmongery schedule which is itself unfrozen per F-002. | Issue tender addendum amending §12.15: (a) reference compliance with I.S. EN 13637:2015 cat 'electrically controlled exit system' for all external doors; (b) specify BGU Grade 1 to BS EN 50130-4; (c) specify 15-second time delay programmable per cause-and-effect; (d) specify fail-safe operation on fire alarm activation (mag drop on FA); (e) cross-reference Arch Ironmongery Schedule AR-40010 (note: still unfrozen per F-002 - hold for ironmongery freeze); (f) require door-by-door schedule submittal showing each access-controlled door, maglock type, BGU presence/absence, time delay setting, FA interlock; (g) cause-and-effect entry per door (see E-002). | Spec §12.15 lists components: 'Door network controllers, Power supply units, Battery Units, Resettable Green Break Glass Units, Touch to Release switches, Slimline magnets complete with safety wires.' No reference to I.S. EN 13637:2015. No 15-second time delay specification (per Fire report Note 9). No identification of which doors get BGU vs simple fastening (per Fire report Note 10 - therapy rooms with direct external exit do NOT require BGU). No coordination reference to Arch Ironmongery Schedule AR-40010. Fire report Note 9 states: 'maglock with BGU Grade 1 - 15 second time delay' at multiple doors. | Spec: §12.15 ¦ Drawings: 1743_68(00) Protective Services, AR-40010 Ironmongery & Access Control | EE_DESIGNER | OPEN
E-016 | MED | ELECTRICAL | Lighting Design / CIBSE LG2 / EN 12464-1 | Electrical Specification + drawings | No lighting design lux schedule or LPD compliance evidence - spec relies on generic 'CIBSE code for interior lighting' reference, no LG2 healthcare specifics, no TGD L energy compliance demonstration | CIBSE LG2 Lighting in Healthcare Premises; EN 12464-1:2021 Indoor work lighting; TGD L 2022 Buildings Other Than Dwellings (energy efficiency, lighting power density); HBN 00-01. | TGD L non-compliance flagged at BER assessment - building cannot achieve compliance certificate. Wrong lighting in sensory rooms (must be dimmable, tunable, low-flicker for users with sensory processing differences). Glare hazard in therapy rooms (must meet UGR limits). Energy performance regulatory failure. | Issue tender addendum: (1) Add §10.18 'Lighting Performance Schedule' room-by-room table per CIBSE LG2 and EN 12464-1, listing: room name, design lux at task plane, uniformity Uo, CRI Ra, UGR limit, Tc, special requirements (tunable white sensory room, dimming therapy, instant-on plant rooms); (2) Add LPD calculation Annex demonstrating TGD L 2022 compliance, lumen/W threshold per luminaire ≥100; (3) Specify sensory room luminaires (200-7000K tunable white, 1-100% smooth dimming, low-flicker <5%, RGB feature option); (4) Bill items 63-01 should require photometric submittals at tender close (or post-award). | Spec §10.1: 'The lighting installation and levels shall meet those detailed within CIBSE code for interior lighting and respective lighting guides.' No room-by-room lux schedule. No CRI specification. No glare UGR limit. No tunable white / circadian / dementia-friendly lighting specification for sensory rooms. No Lighting Power Density (W/m²) calculation to demonstrate TGD L 2022 compliance for buildings other than dwellings (target ~5W/m² typical). Luminaire schedule §10.1 lists only 8 generic types (A-H) with wattage, lumen output and DALI - no Tc (colour temperature), CRI, photometric distribution. | Spec: §10.1, §10.17 ¦ Drawings: 1743_63(00) General Lighting | EE_DESIGNER | OPEN
E-017 | MED | ELECTRICAL | Accessibility / Visual Fire Alarm | Electrical Specification + drawings | No visual fire alarm beacons specified for hearing-impaired users beyond brief mention in §12.02 - healthcare day-care must comply with BS 5839/IS 3218 visual coverage for D/deaf users | I.S. 3218:2024 §6 (visual alarm devices for D/deaf occupants and high-noise areas); BS 5839-1:2017 §17 (visual alarm devices to BS EN 54-23); TGD M 2022 §3.7; BS 8300-2:2018 §17; HBN 00-01 inclusive design. | Users with hearing impairment may not be alerted in single-occupancy spaces (accessible WC, shower, sensory room with door closed). Accessibility/equality of life-safety provision compromised. DAC risk. | Issue tender addendum: amend §12.09 to require BS EN 54-23 compliant visual alarm devices in: every accessible WC (W-2.4-15 minimum), every staff WC, every single-occupancy room where a door closes (sensory rooms, therapy rooms with closing doors), reception, kitchen, plant room (high-noise area). Require lux-coverage analysis per BS 5839-1 Annex F. Cross-reference I.S. 3218:2024. | Spec §12.02 General references 'flashing beacons' generically. Spec §12.09 'Fire Alarm Sounder and flashing beacons': 'Internal sounders shall be of the same sound throughout... External sounders shall be weatherproof.' No room-by-room visual beacon coverage requirement. No requirement for visual beacons in accessible WCs (where audible alone is insufficient for D/deaf users in a single-occupancy lockable cubicle - BS 5839 / I.S. 3218 explicit recommendation). No tactile alarm device (vibrating pager) requirement for staff with sensory differences. CRC Omni population includes users with sensory/cognitive differences where visual+audible+possibly tactile is required. | Spec: §12.02, §12.09 ¦ Drawings: 1743_68(00), 1743_68(01) | EE_DESIGNER | OPEN
E-020 | MED | ELECTRICAL | Project Hygiene / Document Headers and C | Electrical Specification + drawings | Header on majority of pages reads 'Tender Issue - Mechanical Services Specification' on an Electrical spec; spec body uses 'Mechanical Contractor' in scope (§2.03) and 'mechanical' inflexion throughout | Document integrity / project brief flagged M-001/M-004 spec filename typo and M&E hygiene. | Tenderer confusion about scope (M v E). Reduces confidence in technical content. Reinforces M-001/M-002 finding pattern. | Issue tender addendum: replace all 'Tender Issue - Mechanical Services Specification' footers with 'Tender Issue - Electrical Services Specification'. In §2.03 replace 'Mechanical Contractor' with 'Electrical Contractor'. In §2.02 replace 'mechanical engineering services' with 'electrical engineering services' (or 'M&E' if both apply). Confirm spec naming hygiene with M-001 to M-004. | Page footer on multiple pages: 'T5 Partnership Ltd. Tender Issue - Mechanical Services Specification' (changes to 'Electrical Services Specification' mid-document around §3, suggesting partial header update). Spec §2.03 Description of Works: 'The Mechanical Contractor shall supply all labour, materials, equipment and engineering services, and Perform all works necessary to install the complete, tested, commissioned and operational Electrical System...' - 'Mechanical Contractor' is wrong here. Spec §2.02 'mechanical engineering services are co-ordinated' - should say electrical. Section header §1.0 'Schedule of Mechanical, Electrical and Lift Drawings' but content is M&E combined drawing register. | Spec: §2.02, §2.03, All page footers | EE_DESIGNER | OPEN
E-022 | MED | ELECTRICAL | BMS Interface / Section 12.14 AOV / Sing | Electrical Specification + drawings | AOV (Automatic Opening Vent) section §12.17 refers to '1st Floor Level' and 'roof access stair' for a single-storey building - drawing/spec inconsistency, plus AOV scope ambiguity | TGD-B 2024 §1.5 smoke ventilation; I.S. EN 12101-2 AOV products; FSC compliance. | Tenderer cannot determine number or location of AOVs. Building geometry mismatch suggests another cut-paste from a multi-storey project. Risk of AOV omitted or duplicated. | Issue tender addendum: rewrite §12.17 to reflect actual building configuration - single-storey with no 1st floor, AOV locations per Arch GA (likely none required for single-storey day-care - confirm with Fire Engineer if any smoke vent required at all). Resolve §12.14 vs §12.17 overlap. Confirm AOV panel supply boundary (Main vs Elec) per bill 68-14. If no AOV required, delete sections and bill item. | Spec §12.17 Smoke Control: 'Smoke Control - Automatic Opening Vents _ 1 No. Systems at 1st floor Level. Electrical Contractor to include for all wiring associated with Smoke Exhaust Automatic Opening Vent Equipment. Both Systems are located at 1st Floor Level.' Section starts '1 No. Systems' but text says 'Both Systems' - internal inconsistency. Per FSC Report and Arch GA the building is SINGLE-STOREY (Ground only) with roof access stair (per Fire report C&E diagram). Spec §12.14 'Automatic Smoke Vents' separately exists. Bill 68-14 'Required attendances and wiring for AOV panel (supplied by Main Contractor)' - so AOV control panel is supplied by Main Contractor not Electrical Contractor. | Spec: §12.14, §12.17, Bill 68-14 ¦ Drawings: 1743_68(00) Protective Services - check for AOV symbols, Architectural Roof Plan AR-11002 | EE_DESIGNER | OPEN
E-025 | MED | ELECTRICAL | Earthing System Declaration / I.S. 10101 | Electrical Specification + drawings | Spec declares 'solidly earthed (TN-S) system' in §4.04 - but ESB Networks supplies in TN-C-S (PME) configuration; this needs confirmation/coordination with ESB Form NC4 / Service Connection Agreement | I.S. 10101:2020+A1:2024 §312 (system earthing arrangements); ESB Networks Conditions of Supply; HTM 06-01. | ESB Networks Ireland typically supplies LV in TN-C-S (PME) - spec assumption of TN-S may be wrong. This affects: bonding strategy (PME bonding requirements §544 if TN-C-S), need for separate earth electrode, RCD strategy. Fault level 50 kA may be over-specified - if actual is 16-25 kA, switchgear is over-spec. If actual is higher, switchgear is under-spec. Both impact tender price and safety. | Issue tender addendum: (1) Request ESB Networks declared earthing system (TN-S or TN-C-S) and confirmed prospective fault current at the proposed point of supply for this site; (2) Amend §4.04 to reflect ESB declaration; (3) If TN-C-S, add PME bonding requirements per I.S. 10101 §544; (4) Confirm switchgear fault rating against ESB declaration plus 25% margin. | Spec §4.04 Rating and service conditions: 'The switchgear shall be designed for continuous operation on a 415 volt, 50 Hz, 3 phase, 4 wire, solidly earthed (TN-S) system, with a maximum fault level of 50 KA.' Spec §4.01 Incoming Electricity Supply: refers to ESB Networks LV connection but doesn't state earthing system reference (TN-S vs TN-C-S vs TT). 50 kA fault level is at the high end of typical LV supply - ESB to confirm prospective fault current. | Spec: §4.01, §4.04 ¦ Drawings: 1743_60(00) Site Electrical, 1743_69(00) MDB Schematic | EE_DESIGNER | OPEN
S-102 | MAJOR | C&S | DRAINAGE | Cl 2309 - SurfaceWaterAttenuation.xlsx | R44-R60 inflow/outflow table | GDSDS Vol 2 §4.2 climate change allowance (currently 20% min, OPW recommends 20% for SAAR<1000 / 30% sensitive); EPA Climate Change Sectoral Adaptation Plan | Calc applies 30% uplift to M100 rainfall and combines with 'urban creep'. While conservative, 30% must be justified by reference to OPW/EPA guidance and Fingal CoCo SuDS Policy; if regulator requires 40% in revised 2025 guidance, attenuation under-sized. Conversely if only 20% required, design over-conservative — neither stated. | Add narrative to calc and submission cover note citing the specific Irish climate change allowance source (OPW Section 2A Pluvial / Fingal Development Plan 2023-2029 / GDSDS rev) and rationale for 30% CC + urban creep combination; confirm acceptable with planning authority. | M100 (mm) incresed by 30% for climate change and urban creep | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Cl 2309 - SurfaceWaterAttenuation.xlsx | CS_DESIGNER | OPEN
S-103 | MAJOR | C&S | DRAINAGE | Cl 2309 - SurfaceWaterAttenuation.xlsx | R60, R77, R94 — storage required vs provided | CIRIA C753 SuDS Manual §24.6 — storage design margin; GDSDS Vol 2 design life | Required attenuation = 96.0186 m³; provided = 98.7 m³ (coarse aggregate only). Margin = 2.7% (≈2.7 m³) which is below recommended ≥10% factor of safety for clogging, ground settlement and modelled IDF uncertainty. Green roof contribution (5.94 m³) is conservatively included in 'sub-total' but green-roof attenuation is event-by-event recharge and should not be additive at peak storm. | Increase aggregate sub-base depth from 700mm by ~100-150mm or extend permeable paving extent to provide ≥10-15% spare attenuation; separate 'attenuation' calc from 'interception'/'treatment' volume claims (currently same volume used three times R85, R90, R95). | Size of attenuation needed = 96.0186 m³ ¦ Total attenuation provided = 98.7 m³ | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Cl 2309 - SurfaceWaterAttenuation.xlsx | CS_DESIGNER | OPEN
S-104 | MAJOR | C&S | DRAINAGE | 12001 + 12005 PROPOSED DRAINAGE + TYPICAL DETAILS | Car park area (470m² permeable concrete + 421m² resin gravel) | GDRCoP §6.5 / CIRIA C753 §26 — pollution interception for car-parking runoff before discharge; TGD H §2.2.7; Pollution Prevention Guidelines PPG3 | Site includes 891m² of trafficked permeable paving serving day-care visitor parking and ambulance/drop-off bays. No oil interceptor, no Class I bypass separator, no pollution treatment volume shown on drawings. Discharge to public sewer of hydrocarbon-laden runoff breaches GDRCoP and may breach Local Authority discharge licence. Pollution incident risk; potential enforcement. | Confirm whether permeable pavement geotextile/sub-base is being relied on as treatment (CIRIA SuDS treatment train); if so document with reference to interception/treatment performance; otherwise add Class I bypass full-retention separator on outfall before connection to public SW. Annotate on dwg 12001. | Permeable Concrete 470 m² ¦ Permeable resin bound gravel 421 m² ¦ (no separator shown) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\12001 - PROPOSED DRAINAGE.pdf | CS_DESIGNER | OPEN
S-105 | MAJOR | C&S | DRAINAGE | 12002 PROPOSED DRAINAGE - Sections | SW01 IL 30.00 / Ground 30.50 — cover = 500mm | TGD H §2.6 + IS EN 1610; CIRIA R128 — min cover 900mm (non-trafficked), 1200mm (trafficked); IS 240/I.S. EN 295 pipe-class consideration | Long section dwg 12002 shows SW01 at IL 30.00 against ground 30.50 (cover = 500mm). FMH01 IL 29.57, cover ≈ 930mm — borderline. SW01 at 500mm cover under landscaped/paved area is below minimum and at risk from frost heave, surface load damage and root ingress. Pipe failure risk during operation. | Re-grade SW01 invert or specify Class S concrete surround/encase to compensate; revise long-section to show concrete protection where cover <900mm; verify all upstream manhole covers against trafficked vs non-trafficked load class (B125 vs D400 EN 124). | proposed ground level 30.5 ¦ proposed invert level 30.00 ¦ SW01 (cover = 0.5m) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\12002 - PROPOSED DRAINAGE - Sections.pdf | CS_DESIGNER | OPEN
S-106 | MINOR | C&S | DRAINAGE | 12001 + 12002 | Foul drain 150mm @ 1:60; SW 150mm @ 1:50 | TGD H Table 1 — 150mm foul self-cleansing min gradient 1:80 (better not flatter); SW 150 min 1:100 | Foul @ 1:60 is steeper than min and acceptable. SW 150 @ 1:50 is unusually steep for short runs — risk of low flow depth / scour at junctions. SW 225 @ 1:60 at downstream end is correct. Steep gradients combined with low DWF may give noisy operation and air-entrainment but not non-compliant. | Confirm hydraulic check (Colebrook-White or Manning) shows v ≥ 0.75 m/s self-cleansing at design DWF; if not, consider reducing gradient or adding flushing manholes per TGD H §1.30. | 150 @ 1/50 (SW); 150 @ 1/60 (foul) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\12002 - PROPOSED DRAINAGE - Sections.pdf | CS_DESIGNER | OPEN
S-107 | MAJOR | C&S | STRUCTURE-GREEN ROOF | 50004 RC Roof slab + 11003 ROOF PLAN | 300mm RC slab, A393 mesh T&B; Green roof 365m² (dwg 11003) vs 297m² (calc R20) | EN 1991-1-1 §6.3.4 imposed loads on roofs; FLL Green Roof Guideline (German de-facto Eurocode reference); EN 1991-1-3 snow; FSC Condition 7 (PV/green roof loading) | Green roof area shown on drainage drawing 12003 = 297m² and on roof plan 11003 = 365m². 23% discrepancy in area means structural roof loading and surface water attenuation may both be based on wrong number. No green-roof type (extensive 60-150 kg/m² vs intensive 200-500 kg/m² saturated) is annotated on structural drawings. Saturated load case may govern flexure and punching at parapet wall locations. | Reconcile green roof area between drawings 11003, 12003, 50004 and calc R20; explicitly state green roof type and saturated unit weight on dwg 50004; provide structural calculation note covering: DL (slab+screed+green roof saturated) + IL (0.6 kN/m² roof access not occupied, OR 4 kN/m² maintenance localised) + Snow + Wind uplift; cross-reference FSC Cond 7. | Green Roof 365m² (dwg 11003) ¦ Green Roof 297 m² (calc R20) ¦ 300 mm RC roof slab 393 mesh top and bottom | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50004 - RC Roof slab.pdf | CS_DESIGNER | OPEN
S-108 | MAJOR | C&S | STRUCTURE-PV | 50004 RC Roof slab | Roof slab loading basis — no PV array loading visible | EN 1991-1-1; FSC Condition 6 (PV loading allowance to be confirmed by C&S) | FSC Round 1 raised PV array loading cross-check requirement. Reviewing dwg 50004 and the Mesh Calculator xlsx, there is no annotation of PV array dead load (typ. 0.15-0.25 kN/m² distributed, point load at fixings), wind uplift on PV (significant in Dublin zone), or ballast vs penetration design. If PVs are subsequently installed without structural allowance, slab + reinforcement may be inadequate. | C&S Designer to issue confirmation note stating either (a) PV loading included with stated kN/m² + edge-zone wind uplift per EN 1991-1-4, OR (b) future PV install will require structural appraisal — and confirm whether (b) is acceptable to Fire/Architect/Client. | 300 mm RC roof slab, 393 mesh top and bottom (no PV loading note) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50004 - RC Roof slab.pdf | CS_DESIGNER | OPEN
S-109 | MAJOR | C&S | STRUCTURE-PARAPET | 50003 Parapet & Canopy Details | Section F — 1675mm reinforced concrete U-block parapet @ 1200 c/c piers, 2T16 | EN 1991-1-4 + Irish NA: basic wind speed Dublin ≈ 26-27 m/s; EN 1996 Part of masonry; EN 1992-1-1 minimum reinforcement for cantilever; TGD A | Parapet is 1.675m tall masonry with reinforced piers at 1200 c/c, U-block at top with 2T16. Wind moment at base of a 1.675m parapet at q_p ≈ 1.05 kN/m² (Dublin 25m height) with cpe = 1.4 (edge zone) = approx 3.4 kN per m height -> ~4.7 kNm/m base moment, ~5.6 kNm pier moment at 1.2m c/c. 2T16 in 215mm U-block reinforced pier is likely OK in flexure but no calc shown; connection of pier bars into RC roof slab edge not detailed — pull-out / lap insufficient risk. | Provide parapet wind-loading and overturning calc (independent of attenuation calc); detail pier starter-bar lap from RC slab edge into U-block pier (min lap 40Φ = 640mm for T16); confirm BS EN 845-1 connectors/wall-ties for outer brick leaf at parapet. | Reinforced concrete Ublock 2T16 bars ¦ Use hollow blocks to create reinforced piers @1200c/c ¦ 1675mm height | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50003 - Parapet & Canopy Details.pdf | CS_DESIGNER | OPEN
S-110 | MAJOR | C&S | STRUCTURE-CANOPY | 50003 + 50009 Canopy | Section H — 152UC23 stub + 250x250x15 plate + 4 No M16 chemical anchors @ 60mm edge | ETAG 001 Part 5 / EAD 330232 — post-installed mechanical/chemical anchors; EN 1992-4; manufacturer ETA edge distance c_min typ. 100-150mm for M16 chemical | Detail H notes '4No M16 Chemical anchors 60mm min from concrete edge'. Standard ETA for M16 resin anchors requires c_min ≥ 8d = 128mm to achieve full design tension; at 60mm the design tension may be reduced by 50-70% and concrete cone breakout may govern. Canopy is publicly-accessible (children/visitors) — failure consequence severe. | Re-detail with anchor edge distance per anchor ETA (likely ≥120mm); OR increase plate size / move anchors inboard; OR substitute with cast-in welded studs/Halfen channel. Provide anchor design calc to EN 1992-4 with reference to specific ETA number. | 4No M16 Chemichal anchors ¦ 60mm min from concrete edge | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50003 - Parapet & Canopy Details.pdf | CS_DESIGNER | OPEN
S-111 | MAJOR | C&S | STRUCTURE-CANOPY | 50009 STRUCTURE FOR CANOPY | Structural Framing Schedule — 52 No UC152x152x23 marks 1-53 | EN 1991-1-4 wind; EN 1993-1-1 + Irish NA; IS EN 1090-2 Execution Class 2; PSCS Safety File requirements | Canopy schedule lists 52 UC152x152x23 (S355 to spec) cut to wildly varying lengths 654-3740mm. No structural plan showing supports, no load take-down, no connection design at the 150x5 sheet-edge-plate-to-UC weld; weld is 100mm long 5mm fillet — pcap ≈ 5 × 100 × 0.6 × 360/sqrt(3) = 62 kN per side which may not satisfy wind uplift on edge zone of curved canopy. Construction-stage stability of curved edge plate not demonstrated. | Provide full canopy structural calculation set including wind action (cf,0 for free-standing canopy per EN 1991-1-4 §7.3, ψ overall force coefficient with blockage), weld design to EN 1993-1-8, and erection sequence. Schedule to identify each UC by gridline reference; current numbering 1-53 with no plan key is ambiguous for site setting-out. | 100mm long 5mm welds top and bottom ¦ UC152x152x23 (52 No varying cut lengths) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50009 - STRUCTURE FOR CANOPY.pdf | CS_DESIGNER | OPEN
S-112 | MAJOR | C&S | STRUCTURE-BOUNDARY | 50001 1.8m Boundary wall details | Section A — 215mm brick + 337mm conc block rising wall on 900x300 strip, 1 layer A393 | BR 401 frost penetration min foundation depth 450mm Ireland; EN 1996-1-1 lateral stability free-standing masonry; EN 1990 partial factors | 1.8m high free-standing brick wall on 900x300 strip foundation. Section A shows foundation depth not dimensioned. Wall is 215mm brick width (single skin) over 337mm block plinth — slenderness ratio at 1.8m unrestrained, in Dublin Cat II terrain wind zone, requires either thicker wall, piers, or designed reinforced wall. 4.5m expansion joint spacing OK for thermal/moisture per EN 1996; lateral wind not checked. Foundation depth, ground bearing, and earth retention behaviour vs adjacent residential gardens not addressed. | Add foundation depth dimension (min 450mm below ground); provide masonry stability calc to EN 1996-1-1 for 1.8m unrestrained free-standing wall with piers if needed; verify no earth retention at neighbours' gardens (or if there is, redesign as retaining wall per S-012 logic). | 215mm width 1800mm high Brickwall ¦ 900x300 strip foundation 1 Layer A393 mesh | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50001 - 1-8 m Boundary wall details.pdf | CS_DESIGNER | OPEN
S-113 | MAJOR | C&S | REINFORCEMENT | Bending_Schedule.xlsx + 50007 External Stair + 50004 RC Roof slab | Bar mark 01 used multiple times across separate drawings | BS 8666:2020 §6 — bar mark uniqueness within scheduling document; ISTRUCTE Manual for the design of concrete building structures §15 | Bar mark '01' appears on dwg 50007 External Stair as '7-H16-01' (length 6000), on dwg 50004 as cantilever bar, on RC0001 Sheet 01 as '4-H16-01' (perimeter beam). Bending Schedule sheet shows Bar Mark 1 = 16dia × 6000 length × 321 quantity, with 'TO TRIM ON SITE'. Bar marks must be unique per BS 8666 — same mark used for different structural functions risks bender supplying wrong shape/length to wrong location. | Re-number bar marks with element-prefix (e.g. R01 for roof bar mark 1, S01 for stair) OR issue separate schedules per element with element-specific bar marks; 'TO TRIM ON SITE' is contrary to BS 8666 fixed-length scheduling principle — convert to fixed cut lengths to suit detail. | Bar Mark 1 16dia 6000mm 'TO TRIM ON SITE' Qty 321 ¦ 7-H16-01 (stair) ¦ 4-H16-01 (beam) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Bending_Schedule.xlsx | CS_DESIGNER | OPEN
S-114 | MAJOR | C&S | REINFORCEMENT | Bending_Schedule.xlsx | Sheet header — Drawing Number, Revision, Checked By, Approved By all blank | BS 8666:2020 §4 + ISTRUCTE Standard Method of Detailing Structural Concrete §3 — schedule must show drawing reference, status, checker and approver; IS EN 13670 §6.2 inspection regime | Schedule header: Drawing Number = blank, Revision = blank, Checked By = blank, Approved By = blank, Date 30.03.2026. Quantity = 4,313 bars totalling 11.3 tonnes of reinforcement going to bender with no verifiable issue control, no checker signature. If bender works to this schedule contractor has no traceable record; checker (BS 8666 'Type 2 check') not evidenced — non-compliant with QA expectations under SI 9/2014 / BCAR Form ANC. | Issue rev-controlled schedule with explicit drawing reference (each bar mark linked to source dwg + revision), checker signature, approver signature before tender; align bender quantity totals with floor/foundation/roof drawing call-ups (currently 11,278 kg total). | Drawing Number: (blank) ¦ Revision: (blank) ¦ Checked By: (blank) ¦ Approved By: (blank) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Bending_Schedule.xlsx | CS_DESIGNER | OPEN
S-115 | MAJOR | C&S | STRUCTURE-MESH | Foundation Sheets Mesh Calculator.xlsx + 11002 GROUND FLOOR PLAN | Sheet1 R19 Floor Slab 150 thick, 1 layer mesh; dwg 11002 calls A142 | EN 1992-1-1 §9.3.1.1 minimum reinforcement; IS EN 13670 §7; ConcreteCentre TR34 ground supported floors (where applicable) | Floor slab specified as 150mm with A142 mesh (single layer). A142 = 142 mm²/m = 0.095% nominal. With healthcare daycare loading (4 kN/m² IL + equipment), 150mm slab with A142 single layer top-only (or unspecified position) is at lower bound of structural requirement and provides limited crack control across long bays. Calc sheet uses '1 layer A393' (sheet R5) but drawing 11002 specifies A142. Direct contradiction. | Resolve A393 vs A142 contradiction between Foundation Mesh Calculator (A393) and Ground Floor Plan dwg 11002 (A142); confirm position (top vs middle vs bottom), cover, and demonstrate crack-width compliance ≤0.3mm (EN 1992-1-1 §7.3.4) for ground-floor slab under daycare loading. | Mesh type A393 (calculator) ¦ A142 Steel fabric reinforcement (drawing 11002) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Foundation Sheets Mesh Calculator.xlsx | CS_DESIGNER | OPEN
S-116 | MINOR | C&S | STRUCTURE-MESH | Foundation Sheets Mesh Calculator.xlsx | R6 — 15% lost (waste factor) | ConcreteCentre/RC Council best-practice; typical waste 15-20% rectangular slabs, 25-30% complex/curved | Calculator applies flat 15% mesh waste. Roof slab and floor slab geometry per architectural plans is highly curved/irregular (organic forms — see GFP and roof plan 11003); 15% waste is optimistic. Real wastage 25-30% likely. Risk: under-ordering of mesh, programme delay during construction while additional mesh procured. | Increase waste factor to 25% for curved roof slab area (174 sheets becomes ≈ 195), and 20% for foundation strip (54 sheets becomes 60). Issue revised tender quantity to contractor to avoid claim. | 15% lost ¦ 9.792 (effective sheet area) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Foundation Sheets Mesh Calculator.xlsx | CS_DESIGNER | OPEN
S-117 | MAJOR | C&S | STRUCTURE-STAIR | 50007 External Stair | Stair plan view, longitudinal section, Section Q | TGD K Stairs/Ladders/Ramps + TGD M Access; EN 1991-1-1 Cat C3 (Healthcare) imposed loads | External stair drawing 50007 shows stair flight rising into reinforced 215mm solid block walls with 250mm thick RC walls forming a stair compartment. The building is single-storey day-care — purpose of the stair is unstated (plant access? roof access for PV/MEP? maintenance?). No: handrail/balustrade detail; no slip-resistant nosings; no headroom (TGD K 2m min); no top landing fall-protection. If for public/staff use, fails TGD K; if for restricted maintenance, must be locked-off and signed. | Confirm intended use of external stair (public access vs maintenance only); if maintenance, specify locked access, edge protection at top landing, fixed access ladder per BS EN 14122 may be alternative; if public, add full TGD K compliance set — handrail 900-1000mm, balustrade 1100mm, slip-resistance, going 220-300, rise 150-180. | External Stair (purpose not stated) ¦ 215mm thick Solid block | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50007 - External Stair.pdf | CS_DESIGNER | OPEN
S-118 | MINOR | C&S | STRUCTURE-OPENINGS | 50008 General Openings | Typical section at normal size opes; Section 22 | EN 1996-1-1 §6.1.2 lintel bearing; EN 845-2 prefabricated lintels; TGD A; fire rating where over fire doors (TGD B) | Drawing 50008 shows generic 'lightweight stainless steel prefabricated units... 150mm bearing both side' over openings up to 2000mm wide / 4kN max. No: lintel type designation (e.g. IG L1/S-100, Catnic CG70); no opening size schedule; no detail for openings >2000mm; no fire rating for lintels over fire-rated doors/screens (FSC requires 30/60min where over compartment boundaries); no thermal bridge analysis at lintel. | Issue lintel schedule cross-referenced to Architect's opening schedule with: type ref, span, bearing, load, fire-rating where required, U-value/Psi-value confirmation; detail openings >2000mm with bespoke steel/concrete lintel or padstone calc; coordinate with Fire Engineer for opening locations on compartment walls. | Lightweight, stainless steel and prefabricated units used over small openings ¦ 2000mm max wide 4KN max allowed ¦ (no lintel schedule) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50008 - General Openings.pdf | CS_DESIGNER | OPEN
S-119 | MAJOR | C&S | DRAINAGE-FOUNDATION | 11001 FOUNDATION PLAN + 12001 PROPOSED DRAINAGE | 1200x300 + 900x300 strip foundation; drainage runs adjacent/under building footprint | TGD C §3; IS EN 1610 trenchless/trench excavation near foundations; CIRIA C760 — proximity of services to foundations (45° influence zone) | Foundation plan 11001 shows 900-1200mm wide strip footings on 'undisturbed firm soil' (note 7). Drainage plan 12001 shows multiple FMH and SW runs crossing close to building footprint. Without G.I. report (S-008 CRITICAL — confirmed missing) the bearing capacity is unknown; trench excavation for drains within 45° zone-of-influence of foundations is high-risk and may require concrete protection or bridging. No coordination notes between drainage and foundation drawings. | Once G.I. report is received (RFI S-008), add note to dwg 11001 stating allowable bearing pressure, founding stratum and required trench-of-influence protection where drains pass within 45° of underside of foundation. Add concrete encasement/sleeve detail for drain crossings. | Foundation formations to be in the following soil stratum(a) (see soil investigation report): Undisturbed and firm soil | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\11001 - FOUNDATION PLAN.pdf | CS_DESIGNER | OPEN
S-120 | MAJOR | C&S | DRAINAGE | 12005 PROPOSED DRAINAGE TYPICAL DETAILS | Typical Manhole Detail — 'reinforced concrete base C30/37, 75mm blinding' | Irish Water Code of Practice for Wastewater Infrastructure §4 manhole construction; IS EN 1917 / EN 13598; IW-CDS-5030-03 | Manhole detail is generic 'reinforced concrete base C30/37, blockwork chamber, engineering brickwork'. Irish Water now require precast manholes to IS EN 1917 with sealed channel inverts as default. Block manholes only permitted in specific cases with Irish Water approval. Detail also shows no benching geometry, no step-iron pattern, no safety chains, no cover-level adjustment. Risk of Irish Water rejection at compliance certification stage. | Replace typical manhole detail with Irish Water Standard Detail IW-CDS-5004 (precast concrete manhole) and IW-CDS-5005 (cover & frame); annotate channel benching min 25mm above soffit, step pattern per IS EN 13101, and cover Class D400 for trafficked / B125 elsewhere. | TYPICAL MANHOLE DETAIL ¦ REINFORCED CONCRETE BASE GRADE C30/37 ¦ 75 mm BLINDING CONCRETE ¦ ENGINEERIN BRICK WORK | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\12005 - PROPOSED DRAINAGE TYPICAL DETAILS.pdf | CS_DESIGNER | OPEN
S-121 | MINOR | C&S | DRAINAGE | 12005 PROPOSED DRAINAGE TYPICAL DETAILS | Pipework penetrating block walls / RC walls | TGD H §3.21 differential settlement; BR 211 Radon — sealing penetrations; TGD C radon barrier integrity | Detail shows compressible sealant and 'rigid sheet material' both sides at wall penetrations. Good practice for differential settlement but no specific sealant type (e.g. butyl, polysulphide), no fire-stopping reference (penetration through compartment wall requires intumescent collar/wrap to TGD B), and no radon-membrane lap detail at penetration (TGD C §1.3 + BR 211). | Add specification reference for sealant (e.g. Hilti CP 606 or similar approved with fire rating where required); cross-reference radon barrier detail at pipe penetration with continuous EPDM puddle flange or proprietary collar. | Fill Sleeve with compressible sealent to prevebt ingress of gas ¦ Massk opening both side with rigid sheet material | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\12005 - PROPOSED DRAINAGE TYPICAL DETAILS.pdf | CS_DESIGNER | OPEN
S-122 | MINOR | C&S | REINFORCEMENT | Bending_Schedule.xlsx | Bar 3 (16dia shape 51 length 2450 qty 1250); Bar 14 (16dia shape 11 length 1275 qty 180) | BS 8666:2020 Table 2 shape codes; EN 1992-1-1 anchorage and bond | Bar 3 = 16mm shape code 51 (stirrup/link). 1,250 No links of total length 2450mm sums to >3km of links — appears to be RC wall links (250 RC wall typical section shows H10 @250). However Bar 3 is 10mm dia not 16 — schedule entry shows '16' in diameter column but Bar 3 row is annotated 10mm in Sheet1. Probable transcription error in schedule. Sheet1 R3 actually shows 10mm and 2450 length — must verify consistency throughout schedule. | Independent BS 8666 'Type 2 check' of full schedule by competent person; specifically verify bar diameters for marks 3, 14, 16, 17, 18, 20, 21, 22 (shape codes 11/51 stirrups/links that typically use 8-10mm not 16mm); re-issue corrected schedule. | Bar Mark 3 Diameter 10 Shape Code 51 (in Sheet1) ¦ corresponds to Bar 3 in main schedule | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Bending_Schedule.xlsx | CS_DESIGNER | OPEN
S-123 | MAJOR | C&S | STRUCTURE-RC-WALLS | 50005 RC Walls (Typical) | Multiple RC wall types A-H; concrete grade / cover / exposure class not stated | EN 1992-1-1 §4.4 nominal cover; Irish NA Table 4.4N; IS EN 206 exposure classes XC1/XC3/XC4 dependent on location; IS EN 13670 execution | Drawing 50005 details RC walls Type A (600mm), B (800mm), C-H corners/curves with H16 main bars and H10 links @ 200-250mm. No concrete grade stated on this drawing (only on manhole detail = C30/37). No exposure class. No cover. RC walls are partly retaining (rear retaining wall S-012) and partly internal (under green roof — XC3); without grade, cover and exposure class, contractor cannot price, durability cannot be demonstrated to EN 1992-1-1 §4.4 / IS EN 206. | Add specification table to dwg 50005 covering: concrete grade (typ C32/40 for retaining wall, C30/37 internal); exposure class per location; min nominal cover (35-50mm depending on exposure + Dc_dev 10mm); curing/execution per IS EN 13670 Inspection Class 2. | (Drawing 50005 contains no concrete grade, exposure class or cover specification) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\PDF DRAWINGS\50005 - RC Walls (Typical).pdf | CS_DESIGNER | OPEN
S-124 | MAJOR | C&S | REGULATORY | Bending_Schedule.xlsx + project number 'CL2309' | Schedule project number CL2309 + Cl 2309 in surface water calc filename | TII Specification for Road Works Series 2300 — Clause 2309 covers drainage outfall structures for ROADS; not appropriate for healthcare buildings — Building Regs + Local Authority SuDS Policy govern | Surface water attenuation calc is filenamed 'Cl 2309' (TII Spec for Road Works Clause 2309). TII Series 2300 governs national road drainage outfall structures, not healthcare buildings on local roads. Use of TII clause as the basis of drainage design for this site introduces a regulatory mismatch — Fingal CoCo SuDS policy and GDSDS govern. May be benign (just an internal reference) but indicates the calc was likely cloned from a roads job and not fully re-baselined. | Rename calc and update header to cite GDSDS / Fingal CoCo SuDS Policy / CIRIA C753 as design basis; remove TII Clause 2309 reference unless specifically required by Council for any TII-network discharge interaction. Reconfirm methodology alignment with the cited Wallingford Procedure / FSR. | Project: HSE Day Centre 57 Rathbeale Rd ¦ Job No.: CL 2309 ¦ (filename: Cl 2309 - SurfaceWaterAttenuation.xlsx) | C:\Users\gavin\Downloads\02.40.3 Stage 2C Drawings and Reports_selected_2026-05-27_12-59-35pm\Appendix B - Civil and Structural\SCHEDULES\Cl 2309 - SurfaceWaterAttenuation.xlsx | CS_DESIGNER | OPEN

## CRITICAL Items
CRITICAL findings — must close before 10-Jun-2026
ID | Discipline | Doc / Section | Operational risk | Recommended action | Owner
A-009 | ARCHITECTURAL | Architectural Works Specification Section K10 clauses 115A/115B/115C/115D (and K10/145 wall lining) | Spec defines every dry-lining partition (Wall Types 1-4) as 'REI 30 or better' only, with no 60-minute compartment wall type. Contractor will tender on REI 30, leaving the compartment walls required by the FSC un-priced; on site this becomes a Compensation Event under PW-CF5 Clause 10.6 and exposes the project to a non-compliant FSC implementation and BCAR Ancillary Certificate refusal. | Insert a new clause K10/115F 'Compartment Wall Partition - REI 60' (single or twin row studs to suit, 2 x 15mm Type F plasterboard each side, mineral wool 50mm, full Appendix A detail set including head, base, abutment and service-penetration treatment per TGD-B 2024 §3.5.7). Annotate each partition type on a Wall Types plan against fire-cert designation. Issue as Tender Addendum. | ARCH_DESIGNER
A-010 | ARCHITECTURAL | Architectural Works Specification (and Sanitary Schedule 40006) N13 Sanitary appliances; N25 Permanent access and safety equipment; Sanitary Schedule 40006 (Item HOI001) | Sanitary Schedule 40006 (room 0.06 C/P WC) lists 'HOI001 - TRACK HOIST - ceiling mounted H style full coverage of space'. Architectural Spec (N13 and N25) is silent on manufacturer, SWL, voltage, charging point, track configuration, structural pad-stones/back-plates, and commissioning standard. Project brief flags an unresolved CARBITAN vs ARJO vs SEA conflict from earlier issues — none of the three is in the current Arch Spec. Contractor will price the cheapest generic hoist, the Structural design will not have a co-ordinated bearing pad, and HIQA registration will be refused on opening. | Add new clause N25/220 'Ceiling-mounted Patient Hoist System' naming the approved manufacturer (HSE Estates currently approves ARJO Maxi Sky 2 or equivalent), SWL 200kg minimum, full ceiling-track coverage of room 0.06 plus traverse to adjacent shower, with structural reaction loads (typically 2.5 kN point load each track support) to be co-ordinated with Structural Engineer prior to slab/ceiling pour. Reference HBN 00-02 and HSE Estates Buildings Technical Note BTN-04 (Hoists). Confirm in writing with Employer which of CARBITAN / ARJO / SEA is the governing brand and freeze in Tender Addendum. | EMPLOYER
A-011 | ARCHITECTURAL | Architectural Works Specification Section N15 'Internal fire and safety signage systems', clause 270 'Fire performance' | Specifying Class C for escape signage substrate is sub-compliant with TGD-B 2024 for materials lining protected escape routes. Refusal of BCAR Certificate of Compliance on Completion or FSC enforcement action would follow. | Amend N15/270 to: 'Reaction to fire: Standard: To BS EN 13501-1; Class B-s1,d0 to all escape signage substrates and any photoluminescent backing.' Cross-reference with Fire Strategy Report Cond. 3. | ARCH_DESIGNER
A-100 | ARCHITECTURAL | Windows & External Doors Type Elevations & Schedules Drawing 11606-XX-XXX-SH-RHA-AR-40002 | PDF file at 40002 contains stair-section content only — no window types, no external door schedule, no glazing spec, no U-values. Tenderers cannot price windows, ext doors, glass, ironmongery to ext doors, or trickle vents. Issuing pack at tender is non-compliant and will trigger a tender-stage RFI on the highest-cost facade element. | Re-issue 40002 with the correct content: Window Types W0.001–W0.0xx (frame system, glazing make-up, U-value W/m²K, g-value, opening lights, restrictor, manifestation, trickle vent area), External Door Types XD0.0xx (leaf, glazing, threshold, ironmongery set ref, security rating, U-value), Window Boards, integrated blind cassettes, and full coordinated Schedule. Confirm before 10-Jun tender issue. | ARCH_DESIGNER
A-101 | ARCHITECTURAL | Curtain Walls Type Elevations & Schedule Drawing 11606-XX-XXX-SH-RHA-AR-40003 | PDF 40003 also contains only stair content — no CW-01, CW-09 (referenced on Elevations 20001) elevations, no schedule, no spider/transom/mullion details, no spandrel make-up. Highest visual-quality facade element is unpriceable. Will create variation exposure post-award. | Issue corrected 40003 with: CW-01…CW-NN bay elevations at 1:25, glazing make-up table (U-value, g-value, acoustic Rw), aluminium colour ref, structural sealant/cap details, slab-edge fire-stopping (TGD B Vol 2 ref), interface to brick reveal, integrated blinds (if any). Cross-reference all CW marks on Elevations sheet 20001. | ARCH_DESIGNER
A-102 | ARCHITECTURAL | C/P WC Room Layout & Sanitary Schedule Room 0.06, Drawings 60006 + 40006 | Sanitary schedule for Room 0.06 lists WCH005 'CANTILEVER, hospital pattern' (wall-hung corner WC) — NOT a peninsular WC. Changing Places certification requires a peninsular pan accessible from both sides for hoist transfer. As specified, the C/P WC fails Changing Places certification and HIQA registration of the unit will be at risk. | Replace WCH005 in Room 0.06 with peninsular WC (e.g. AKW Livenza-P or equivalent) projecting 800mm from rear wall with 1000mm clear each side; reissue 60006 plan and sanitary schedule 40006. Confirm with HSE Estates that CR2C unit must be 'Registered Changing Places' (not just enhanced accessible WC). | ARCH_DESIGNER
A-103 | ARCHITECTURAL | C/P WC Room Layout & Sanitary Schedule Room 0.06, Drawings 60006 + 40006 | Sanitary schedule 40006 for Room 0.06 omits BNH900 (changing bench) from the list — only shown as a 2D symbol on elevations of 60006. As tendered, no specification, no SWL, no actuator, no fixings; bench cannot be priced or installed correctly. C/P WC will not be commissionable. | Add adult-sized height-adjustable changing bench to sanitary schedule 40006 Room 0.06: e.g. Pressalit R8581 or equivalent, 1800×800mm, electric, SWL 200kg, with control pendant, including fixing to engineered backing plate (cross-ref ARCH details for structural pull-out). Confirm electrical supply, IP rating, and BS EN 60601 compliance. | ARCH_DESIGNER
A-107 | ARCHITECTURAL | Internal Finishes Schedule — Kitchen 0.17 Drawing 40009 row 0.17 | Kitchen 0.17 walls specified as 'Washable matt emulsion paint, enhanced durability, Colour - White'. Paint is absorbent, not impervious, fails Reg 852/2004 Annex II Ch I. EHO will not pass kitchen at HIQA registration. Re-clad cost in occupation phase. | Change Kitchen 0.17 wall finish to PVC hygienic wall lining (Altro Whiterock Satins or equiv) full height to ceiling, welded seams, coved to floor and ceiling, behind appliances and at splashback. Update 40009 row 0.17. Match approach already used in WC/Shower/Cleaners Store rows. | ARCH_DESIGNER
C-001 | CONTRACT/PACK | Multiple — Arch register, M&E issue sheet, Fire Stage 2C report Project title block / header across all 3 packs | Three different project descriptors create ambiguity over what is being tendered. At award, the executed contract may reference a description that does not match drawings or specifications, creating dispute potential and challenging BCAR compliance. | Issue a single project descriptor instruction: '57 Rathbeale Road CRC Children's Disability Network Team — Day Care Centre, Swords, Co. Dublin K67 EP62'. Update all discipline pack title blocks to this exact descriptor before tender issue. Confirm legal Employer entity (HSE per M&E sheet vs. CRC per project brief vs. Building Owner) on FOT Schedule Part 1. | EMPLOYER
C-002 | CONTRACT/PACK | All discipline registers Issue dates across discipline packs | Tender pack is not a single coherent issue. Tenderers cannot rely on a single 'issue date' as the price-baseline. Variations may be claimed against information issued at different times. | Reissue all discipline packs to a single coordinated tender issue date with consistent revision codes. State 'Issued for Tender — DD-MMM-2026' on every title block. Lock CDE issue date. | ER
C-003 | CONTRACT/PACK | Fire Part B Compliance Report (22481-Stage 2C Report) Notes 12-15 (p.5) | Existing granted FSC dated 19/08/2025 with 7 conditions. Design changes 31/03/2026 (external store under stairs, bin→bike store, Activity Room 13 reconfig) formally determined by SFPO Keith Boland 08/04/2026 to require REVISED FSC and DAC. Tenderer must price for revised FSC submission process AND for compliance with both the original 7 conditions and any conditions on the revised grant. Commencement may issue on existing FSC, but occupation is blocked until revised FSC and DAC are granted. | (1) Add explicit clause in Preliminaries: 'Contractor shall allow for compliance with the granted FSC and its 7 conditions, and shall allow for cooperation with Design Team submission of revised FSC and DAC during construction. Occupation is contingent on grant of revised FSC and DAC.' (2) Issue all 7 FSC conditions as a tenderer-facing schedule. (3) Confirm position on Activity Room 13 / bike store / external store scope freeze before tender issue. | ER
E-100 | ELECTRICAL | Electrical Specification §2.05 Standards, Rules and Regulations / §4.02 / §4.04 | Spec lists BS 7671:2018 (UK standard), ETCI Rules, IEE Wiring Regulations 16th Edition, BS 5486, IEC 144, BS 5420, BS 6346:1989, BS 8724:1990, BS 4568-1970 etc as primary references. Contractor is contractually obliged to comply with these obsolete/non-Irish standards. Risk of installation being non-compliant with FSC Cond 6, RECI/SafeElectric refusal to certify, and HSE refusal to accept handover. Cost & programme impact during construction once non-conformance is discovered. | Re-issue Sections 2.05, 4.02, 4.04, 4.05, 4.06, 4.09, 4.17, 5.01, 5.02, 5.03, 5.04, 5.06, 5.07, 6.01, 7.01, 7.03, 8.02, 10.01, 12.00 with all references aligned to I.S. 10101:2020+A1:2024. Delete BS 7671:2018, ETCI, IEE 16th Ed references. Replace BS 5486 with I.S. EN 61439 series. Replace BS 6346/BS 8724 with current IEC/EN cable standards. | EE_DESIGNER
E-101 | ELECTRICAL | Electrical Specification §4.04 Rating and service conditions | Spec states 'a 415 volt, 50 Hz, 3 phase, 4 wire, solidly earthed (TN-S) system, with a maximum fault level of 50 KA'. ESB Networks in Ireland generally provide TN-C-S supply. TN-S is rare and would require dedicated cable from substation. Earthing design (sizes of CPC, supplementary bonding, RCD strategy) is fundamentally different between TN-S and TN-C-S. Also 50 kA fault level is unverified for a small day-care centre — typical ESB cut-out fault current at LV is 16–25 kA. Over-specifying switchgear adds cost; mis-specifying earthing system creates safety risk. | Obtain ESB Networks Quote/Connection Offer confirming (a) earthing system (TN-C-S expected), (b) prospective fault current at the cut-out (PSCC) and (c) external earth fault loop impedance Ze. Re-issue §4.04, §7.0 Earthing with verified ESB data. Confirm switchgear icw rating matches actual PSCC + safety factor. | EE_DESIGNER
E-102 | ELECTRICAL | Drawing 1743_69(01) — SDB Schematic SDB 01 & SDB 02 distribution | SDB schematics show generic 30mA RCDs/RCBOs feeding circuits that include EV car charger, PV inverter, heat-pump compressors and VSD-driven MVHR fans. PV inverter and EV charger inject DC residual currents that 'blind' Type AC and Type A RCDs, defeating earth-fault protection — established cause of electrocution. RCBO type (AC / A / F / B) is not stated on any schematic or schedule. Risk: latent loss of earth-fault protection on critical circuits at a healthcare day-care for vulnerable users. | Mark every RCD/RCBO on 1743_69(00), (01) and (02) with mandatory type: Type B at PV AC isolator, EV charger, heat-pump compressor, MVHR VSDs and lift (if any); Type A elsewhere. Add note to spec §4.09 making Type B mandatory for these circuits and prohibiting downstream Type AC. | EE_DESIGNER
E-103 | ELECTRICAL | Electrical Specification §12.20 Lightning Protection System | Specification §12.20 describes the project as 'School Type Building located at Convent Hill, Ballina, Co. Mayo. New Build Concrete and Steel Structure over 2 levels. Ground / 1st + Roof Over. Highest Point of Building above Ground Level _ 11.0 m'. This is verbatim text from a different project. The actual building is a SINGLE-STOREY day-care centre at 57 Rathbeale Road, Swords. Contractor would price lightning protection on wrong building geometry, wrong height, wrong occupancy (Class 'School' vs 'Healthcare day-care'). Direct contradicts FSC Cond 6 evidencing risk assessment for actual structure. This same cut-paste error was flagged in Round 1 and persists. | REJECT spec §12.20 in current form. Re-write specifically for 57 Rathbeale Road CRC Omni Unit: single-storey day-care, ground floor only (no first floor), state actual building height (parapet level), state actual roof area & geometry, state Loss L1 (loss of human life) due to vulnerable healthcare day-users. Provide IS EN 62305-2 risk assessment as appendix to spec. Confirm Down-conductors hidden in wall make-up (currently stated) is consistent with actual single-storey structure. | EE_DESIGNER
E-104 | ELECTRICAL | Electrical Specification §10.17 School Lighting Notes (Primary & Secondary) / §12.16 Wiring for External Vehicle and Pedestrian Gates | Spec §10.17 contains an entire section titled 'School Lighting Notes (Primary & Secondary)' with school-specific clauses: 'no longer a requirement to have manual switching on the row of light fittings nearest the teaching wall', 'two way switching of the classroom lights in the vicinity of the teachers desk', 'In 16 classroom schools and over', 'Principal/Caretaker', etc. §12.16 references 'external gates' likely from another commercial project. Spec also references BoQ items '62-14 classroom trunking system' and induction loops in 'classrooms and GP Hall'. None of this applies to a 12-room day-care centre. Contractor will price phantom scope and dispute later as variation; risk to tender comparability and price certainty. | Delete §10.17 entirely. Strip every reference to 'school', 'classroom', 'Principal', 'GP Hall', 'teaching wall' from spec body and BoQ summary. Re-issue §10.x lighting controls with day-care-specific requirements: tunable white in sensory rooms (DT 0.012), absence detection in therapy rooms, manual-off in administrative areas, daylight harvesting at perimeter zones, CIBSE LG7 §5 lux levels. | EE_DESIGNER
H-001 | HEALTHCARE | 11606-XX-L00-DR-RHA-AR-11001 GA Plan Ground Floor (and ALL drawing title-blocks across the pack) Title-block / Project description | Every drawing in the Stage 2C pack is titled 'Construction of Day Centre for Adults with Disabilities at Rathbeale Road, Swords, Co. Dublin'. The Employer brief (and this review) treat the building as a CRC Children's Disability Network Team day-care centre. The two operational models drive fundamentally different room sizing, sanitaryware, safeguarding, signage and parent/family-zone requirements. If the design has been developed against an 'adults' brief and is now to be operated as a paediatric CDNT, the entire room data sheet basis is wrong — paediatric WCs, basins, vision panels, child window restrictors, parent waiting and changing facilities are all absent. Risk of total brief rework post-tender or, worse, an unsuitable facility delivered to HIQA on day one. | RFI to Employer (HSE Dublin North East) — formally confirm operational user: (a) Adult Disability Day Centre, OR (b) CRC Children's Disability Network Team. Until clarified, all paediatric-specific findings below remain OPEN against ARCH_DESIGNER. If (b) is correct, the entire FF&E and sanitary schedule requires re-issue with paediatric variants and a paediatric/parent-zone gap analysis must precede tender issue on 10-Jun-2026. | EMPLOYER
H-002 | HEALTHCARE | 11606-XX-L00-DR-RHA-AR-53001 C/P WC Laid to Falls + 11606-XX-ZZZ-SH-RHA-AR-40008 FF&E Totals Room 0.06 C/P WC — 14.24 m² | Drawing 53001 shows internal clear dimensions 3356 mm (W) × 4324 mm (D) — width is 644 mm SHORT of the 4000 mm required by Consortium spec. The FF&E schedule (AR-40008) lists ONLY a single ceiling H-track (HOI001), a single privacy screen (SCR960), and grab rails — no height-adjustable changing bench (CAB033 absent), no shower head, no shower valve and no central floor gully are scheduled in this room. The plan shows only WC, basin and a hoist track; the bench is implied by dashed lines but no equipment is specified. As designed the room WILL FAIL Changing Places registration with the Consortium and HIQA accessibility audit; CRC parents will be unable to safely change a teenage or adult-sized service user. | ARCH_DESIGNER to (a) reconfigure room to achieve 4000×3000 mm clear internal — extend wall onto Corridor 02 by ~700 mm or re-allocate ACC WC 0.05 footprint; (b) add electric height-adjustable adult changing bench to FF&E (Pressalit Select R8581 or equal-approved); (c) add overhead shower with central floor gully (drainage already shown laid-to-falls); (d) confirm hoist track covers bench + WC + shower zones (cross-ref with S — ceiling structural loading per BS EN 10535); (e) add Consortium registration intent to specification. | ARCH_DESIGNER
H-003 | HEALTHCARE | 11606-XX-ZZZ-SH-RHA-AR-40006 Sanitary Schedule All Accessible WCs (0.05, 0.09, 0.11, 0.22, 0.29, 0.30) + Cleaners 0.03 + Group Therapy 0.08 + Activity 0.15/0.20 + Dining 0.16 | Sanitary Schedule AR-40006 specifies WCH005 'cantilever 750 mm projection, hospital pattern' (adult pan height ~450 mm) in EVERY accessible WC, and BAS105 (adult small wash basin) throughout. CRC CDNTs serve children aged 0–18 with wide developmental range. There are NO paediatric pans, NO low-level (380–510 mm) child WCs, NO paediatric basins at 600 mm rim height in any room. Children will need to be lifted onto adult pans — fall risk, manual-handling injury risk to staff, dignity breach. HIQA inspectors will cite this on first visit. | Pending H-001 clarification: if CDNT brief confirmed, ARCH_DESIGNER to add minimum one paediatric WC + paediatric basin in each of the two WC clusters serving children's zones (one near Group Therapy 0.08, one near therapy corridor 0.23-0.28). Recommended: Armitage Shanks Contour 21 Junior pan or equal. Update AR-40006 and AR-40007 (IPS panels). | ARCH_DESIGNER
M-102 | MECHANICAL | Drg 1743_57_00 Ventilation Ground Floor + Mech Spec §11 Kitchen (Room 0.31) extract design | Kitchen 0.31 is shown on Drg 57_00 with a single 250mm 360° disc-valve extract of only 114 L/s — equivalent to ~6 ACH for a 35m² kitchen. There is no canopy hood, no grease filter, no separate cooking-zone extract duct, no make-up air, no make-up balance with WCs, and no fire-rated kitchen extract ductwork. IS EN 16282-7 requires 700-900 m³/h per m² of cooking surface (≈300-400 L/s for even a small commercial kitchen). Without a canopy the kitchen will fail HBN 00-04, fail building control sign-off, and create smoke spread risk to dining 0.30. | Issue addendum confirming: (a) kitchen scope — is this a domestic-style preparation kitchen or commercial cooking? (b) If commercial, provide canopy + grease filtration + dedicated extract fan to IS EN 16282-7 + fire-rated stainless ductwork; (c) confirm capture velocity & make-up air strategy; (d) confirm interface with wet-chemical suppression (Ansul or equivalent) and BMS cause-and-effect with fire alarm. | ME_DESIGNER
M-104 | MECHANICAL | Drg 1743_57_00 Ventilation schedules Sensory room / Therapy room / Snoezelen ventilation rates | Sensory rooms 0.26, 0.27 (and Snoezelen) are shown on Drg 57_00 with supply 30 L/s @ NR<35 and 30 L/s extract via single disc valve. For a sensory room with 4-6 users + carers (typical CRC paediatric use) the CIBSE per-person minimum (10 L/s × 8 = 80 L/s) is not met. Therapy rooms (0.12, 0.10) show 30 L/s — again below minima for occupied therapy spaces. There is no demand-control CO2 sensor specified per room despite the variable occupancy profile, and no quiet-mode requirement (sensory rooms must be NR25 not NR35). | Reissue Drg 57_00 air change schedule with per-room CIBSE A and HBN 00-04 demonstration. Add CO2 demand sensor in each sensory & therapy room linked to MVHR via BMS. Specify NR25 acoustic limit for sensory rooms (not NR35) — re-select attenuators if required. | ME_DESIGNER
M-106 | MECHANICAL | Drg 1743_53_00 + Mech Spec §9.03 + §10 Domestic hot water — Legionella control | DHW heat-pump (Mitsubishi QAHV-N560YA, 40 kW, max flow temp 60°C) feeds a 200-litre stainless cylinder per Drg 53_00. No Legionella regime is specified: (i) no 60°C minimum storage stat setpoint, (ii) no weekly 65°C pasteurisation cycle programmed, (iii) no thermometer pockets shown at flow & return, (iv) HWS return circulating temperature requirement (≥55°C at every point) not stated, (v) no chlorine dioxide / Cu-Ag dosing or alternative supplementary control specified, (vi) no Written Scheme of Control or Responsible Person nomination per L8 §2.10. Heat-pump DHW at 60°C is borderline for Legionella control without an electric immersion heater pasteurisation cycle. | Issue addendum: (a) confirm Legionella Written Scheme of Control will be produced by Mech Contractor pre-handover per HSE L8 §2.10; (b) add immersion-heater pasteurisation cycle 65°C weekly to BMS strategy (BMS Drg 59_01); (c) add thermometer pockets at cylinder flow, secondary return, and most-distant outlet on Drg 53_00; (d) add commissioning requirement that secondary return reaches plant ≥55°C at all points; (e) confirm HTM 04-01 Part B sampling regime for first-year occupancy. | ME_DESIGNER
S-008 | C&S | All structural drawings (11001 Foundation Plan, 11002 GF Plan, 11003 Roof Plan, 50001-50009, RC0000-RC0007) Standard NOTES box (notes 3 and 7) on every sheet | Foundation design proceeds on the unverifiable assumption of 'undisturbed and firm soil' with no allowable bearing pressure stated and no Ground Investigation (GI) report referenced anywhere in the C&S pack. Any soft spots, made ground, or perched water at formation level will trigger an unbudgeted redesign (raft / piled solution), claims under PW-CF5 clause 10 (unforeseeable ground conditions), and programme slippage. For a CRC healthcare/day-care facility on a brownfield Swords site, ground conditions cannot be assumed. | Issue RFI to C&S designer to (a) attach the GI/site investigation report to the tender pack with named author, date, borehole/trial-pit log and laboratory schedule; (b) state characteristic and design bearing resistance (kN/m²) and reference Geotechnical Category (GC1/GC2/GC3) per EN 1997; (c) replace the blank 'soil stratum(a)' field in note 7 with the actual stratum identified in the GI; (d) confirm any chemical/sulphate testing for DS class to support concrete exposure selection. If no GI exists this must be commissioned before tender issue. | CS_DESIGNER
S-100 | C&S | Cl 2309 - SurfaceWaterAttenuation.xlsx + 12001 PROPOSED DRAINAGE R41 calc; FMH/SW layout dwg 12001 | Calc fixes max allowable discharge at 2 l/s (cell R41) but QBAR-greenfield for the 0.24 ha site = 1.36 l/s (R31). Designer has adopted 2 l/s without GDSDS / Fingal CoCo / Irish Water consent. If consent is granted only at 1.36 l/s (QBAR), the 75mm Hydrobrake orifice on dwg 12001 and the 96m³ attenuation volume are both under-designed; storage requirement rises to ~110m³ vs 98.7m³ provided — design fails GDSDS. | PM/CS_Designer to obtain written confirmation of permitted discharge rate from Fingal CoCo and/or Irish Water BEFORE TENDER; re-run attenuation calc and resize Hydrobrake at confirmed rate; if QBAR governs, increase coarse aggregate sub-base depth or add geocellular crate to demonstrate ≥10% spare capacity. | CS_DESIGNER
S-101 | C&S | 12001 PROPOSED DRAINAGE Drawing 12001 — 'New SW pipe to council detail' note (top right) | Drawing 12001 shows new SW discharge to 'existing manhole' / 'new manhole to council detail' with no statement whether downstream public sewer is separate-SW or combined. If combined, the connection is prohibited by GDSDS and Fingal CoCo will refuse Section 24 consent — drainage strategy invalid and CSA / tender pricing unreliable. | Issue RFI to Fingal CoCo confirming downstream sewer classification (combined vs separate SW); obtain Irish Water pre-connection enquiry response (PCE) and Connection Agreement; annotate drawing with sewer reference, IL and gradient at point of connection. | CS_DESIGNER
X-001 | FIRE/COORDINATION | Fire Part B Compliance Report (ORS Doc 22481-Stage 2C) Stage 2(c) Notes §12, §13, §14 | The pack being tendered on 10-Jun-2026 contains DESIGN CHANGES (store under external stair, bin-to-bike store conversion, store/breakout reconfiguration in Activity Room 13) which the Senior Fire Prevention Officer Keith Boland confirmed on 08/04/2026 are NOT minor and REQUIRE a revised FSC and revised DAC under §11 SI 496/2009. The contract is therefore being procured against a design that the contractor cannot lawfully complete and occupy. Building cannot be opened until the revised FSC + DAC are obtained — a programme risk that crystallises as an Employer compensation event under PW-CF5 Clause 9.4 (instructed change / time extension) once the revision lands mid-construction. | Before tender issue: Employer's Representative (ER) to instruct ORS Fire and Rhatigan Architects to SUBMIT the revised FSC and revised DAC applications NOW so that grant dates can be tracked. Pack to include an explicit Information for Tenderers note stating: '(a) FSC dated 19/08/2025 governs at tender, (b) Revised FSC and DAC applications submitted [date] reference [BCMS no.], (c) Contractor to allow for and coordinate with grant of revised FSC/DAC prior to building occupation, (d) any consequential design refinement will be handled under PW-CF5 Clause 9 as Employer Change'. Without this, the Employer is procuring a contract it knows is not certifiable as drawn. | ER — Employer's Representative (Rhatigan & Co. acting as Lead Designer / coord.)
X-002 | FIRE/COORDINATION | Architectural Wall & Partition Types AR-15001; Internal Door Schedule AR-40001; Ironmongery Schedule AR-40010; Fire Stopping Details AR-59001-59004 WT1-WT6, WT-B1 to WT-B3, BO-1/BO-2 partition legend; door schedule fire rating column; ironmongery Sets 04, 06, 10A | Wall & Partition Types drawing AR-15001 lists WT1-WT6 and WT-B1 to WT-B3 with sound ratings but EVERY entry for fire rating reads 'Fire Rating: Refer to Fire Cert, Drawing No. 1000A, 1001A & 1002A' — the Fire Cert drawings are NOT included in this tender pack (ORS pack contains only 22481-PFD-XX-00-DR-F-003). Tenderers cannot price compartmentation construction. The bricklayer/plasterboard contractor must know whether a given WT-B1 blockwork run is 60-min, 30-min or non-rated. Compounded by the fact that the door schedule confirms only 4×FD30S + 1×FD60S (Fire Report Note 11) but ironmongery Sets 04/10A include 'Motorised door opener/closer with Magnetic locking device' on the kitchen FD60S — coordination of door + closer + hold-open device must be on a single Ironmongery + Door Type drawing or it will not survive site assembly. | Pre-tender (by 03-Jun-2026): Architect to (a) reissue AR-15001 with explicit fire rating against each WT/WT-B/BO partition type, (b) include the Fire Cert plans 1000A/1001A/1002A in the tender pack OR confirm they are superseded by AR-15001 fully marked-up, (c) cross-reference the 5 fire doors (D0.002 FILE & COMMS, D0.003 CLEANERS STORE, D0.009 KITCHEN, D0.014 STORE, D0.018 ACTIVITY ROOM STORE) to the matching compartment wall lines on AR-15001. Fire-stopping detail sheets AR-59001-59004 are numbered 1, 2, 3, 5 — Sheet 4 is missing from the pack; either reissue or confirm 'not used' on issue sheet. | ARCH_DESIGNER — Rhatigan & Co. Architects (Lead Designer)
X-004 | FIRE/COORDINATION | Mechanical Specification (T5) and Electrical Specification (T5); Arch Kitchen Layout AR-57012 Room 0.17 FSC Condition 5; Mech Spec entire; Elec Spec §12; Arch Kitchen layout | Grep of full Mechanical Specification returns ZERO hits for 'IS EN 16282', 'suppression', 'ansul' or 'kitchen hood' fire suppression. The kitchen serves a healthcare day-care centre (CRC Omni clients with disability) — Condition 5 of the granted FSC mandates a fixed suppression system to IS EN 16282-7 with interlocks to the gas supply, extract fan, fire alarm and (per ironmongery schedule) the FD60S kitchen door's magnetic hold-open device. None of these interlocks is specified — neither in the Mech Spec (extract + hood + supply gas), nor the Elec Spec (interlock wiring + alarm input), nor the Architectural Kitchen layout (mounting/access for the system). A bidder cannot price this scope. | Pre-tender (mandatory): ER to instruct T5 to issue a Kitchen Fire Suppression Specification section covering (a) fixed wet-chemical or equivalent system to IS EN 16282-7, (b) gas solenoid valve fail-closed on activation, (c) hood interlock to extract fan run-on then shutdown, (d) hard-wired signal to fire alarm panel, (e) release of mag-lock hold-open on the FD60S kitchen door (Set 04), (f) annual service regime to feed forward into HSE PCM O&M and HIQA inspection regime. Rhatigan to amend AR-57012 to show suppression bottle/cylinder location and access. Without this, the project fails FSC Condition 5 at first inspection. | ER — T5 Engineering (M&E) + Rhatigan Architects

## By Discipline
Findings by Discipline × Severity
Discipline | CRITICAL | HIGH | MEDIUM | LOW | TOTAL
ARCHITECTURAL | 8 | 24 | 27 | 5 | 64
ARCHITECTURAL/COORDINATION | 0 | 1 | 2 | 0 | 3
C&S | 3 | 11 | 12 | 4 | 53
CONTRACT/PACK | 3 | 0 | 0 | 0 | 3
CROSS-DISCIPLINE | 0 | 1 | 3 | 1 | 5
ELECTRICAL | 5 | 20 | 7 | 6 | 47
FIRE | 0 | 4 | 4 | 0 | 8
FIRE/COORDINATION | 3 | 6 | 3 | 0 | 12
HEALTHCARE | 3 | 7 | 12 | 1 | 23
M&E | 0 | 1 | 2 | 1 | 4
MECHANICAL | 3 | 19 | 20 | 4 | 46
TOTAL | 28 | 94 | 92 | 22 | 268